## 일반
Register | Function code | Permissions | Group size | Description | Data format
1000 | 0x03 | R | 8 | 제품명 | "SPDS-ACQ " (공백 8개 포함 총 16개 characters)
1001
1002
1003
1004
1005
1006
1007
1008 | 0x03 | R | 16 | Serial number | "ACQ-SPDS-K-2022-0001 " (공백 12개 포함 총 32개 characters)
1009
1010
1011
1012
1013
1014
1015
1016
1017
1018
1019
1020
1021
1022
1023
1024 | 0x03 | R | 1 | 펌웨어 버전 | 1.02 --> 0x0102 12.34 --> 0x0C22
1025 | 0x03 | R | 1 | DI #1, #2 | Bit 15 ~ bit 2 : 0 Bit 1 : DI #2 Bit 0 : DI #1
1026 | 0x03 | R | 2 | Alarm indicator | 0x0000 : LED off, 0xFF00 : LED on
1027 |  |  |  | Error indicator | 0x0000 : LED off, 0xFF00 : LED on
1028 | 0x03 | R | 1 | 차단기 동작 이벤트 indicator | 0x0000 : 신규 이벤트 없음 0xFF01 : 신규 이벤트 있음
1029 | 0x03 / 0x06, 0x10 | R / W | 13 | IP address | 192.168 --> 0xC0A8
1030 |  |  |  |  | 10.100 --> 0x0A64
1031 |  |  |  | Subnet mask | 255.255 --> 0xFFFF
1032 |  |  |  |  | 255.0 --> 0xFF00
1033 |  |  |  | Default gateway | 192.168 --> 0xC0A8
1034 |  |  |  |  | 10.1 --> 0x0A01
1035 |  |  |  | Port number | 16-bit unsigned integer
1036 |  |  |  | Local unit의 IP address | 192.168 --> 0xC0A8
1037 |  |  |  |  | 10.100 --> 0x0A64
1038 |  |  |  | 현재 시각 | 32-bit unsigned integer 연월일시분초 (UTC+9)
1039
1040 |  |  |  | 트리거 전 파형 저장 시간 | ms단위의 정수값
1041 |  |  |  | DI debounce time | ms단위의 정수값
1042 | 0x06 | W | 1 | 장치 리셋 Dev Rst | 0xFF00 : 리셋 명령 리셋 명령을 읽은 후 장치에서 값을 0으로 clear
1043 | 0x06 | W | 1 | 차단기 동작 이벤트 Erase | 0xFF00 : Erase 시킴 리셋 명령을 읽은 후 장치에서 값을 0으로 clear
20230608 변경 사항
1. 1028 번지에 이벤트가 있을 때 0xFF00으로 표시 되던 부분을 0xFF01, 0xFF02, 0xFF03, … 하위 1byte에 개수를 표시함
2. 1043번지에 0xFF00을 쓰면 차단기 동작 이벤트 Erase 시킴
2. Writing 0xFF00 to address 1043 erases the breaker operation event.

## 계측
Register | Function code | Permissions | Group size | Description | Data format
1100 | 0x03 | R | 24 | 전압 크기 | 32-bit floating point, IEEE-754 format
1101
1102 |  |  |  | 전압 위상각 | 32-bit floating point, IEEE-754 format
1103
1104 |  |  |  | A상 전류 크기 | 32-bit floating point, IEEE-754 format
1105
1106 |  |  |  | A상 전류 위상각 | 32-bit floating point, IEEE-754 format
1107
1108 |  |  |  | B상 전류 크기 | 32-bit floating point, IEEE-754 format
1109
1110 |  |  |  | B상 전류 위상각 | 32-bit floating point, IEEE-754 format
1111
1112 |  |  |  | C상 전류 크기 | 32-bit floating point, IEEE-754 format
1113
1114 |  |  |  | C상 전류 위상각 | 32-bit floating point, IEEE-754 format
1115
1116 |  |  |  | Trip coil 1 전류 크기 | 32-bit floating point, IEEE-754 format
1117
1118 |  |  |  | Trip coil 2 전류 크기 | 32-bit floating point, IEEE-754 format
1119
1120 |  |  |  | Close coil 전류 크기 | 32-bit floating point, IEEE-754 format
1121
1122 |  |  |  | 온도 | 32-bit floating point, IEEE-754 format
1123

## 차단기동작이벤트
Register | Function code | Permissions | Group size | Description | Data format
1200 | 0x03 | R | 48 | Event number | 0~255
1201 |  |  |  | Event type | Trip=0x55, close=0xAA
1202 |  |  |  | Event time 1 | 32-bit unsigned integer 연월일시분초 (UTC+9)
1203
1204 |  |  |  | Event time 2 | 32-bit unsigned integer ms 단위의 값
1205
1206 |  |  |  | Contact duty A | 32-bit floating point, IEEE-754 format
1207
1208 |  |  |  | Contact duty B | 32-bit floating point, IEEE-754 format
1209
1210 |  |  |  | Contact duty C | 32-bit floating point, IEEE-754 format
1211
1212 |  |  |  | Trip coil 1 peak current | 32-bit floating point, IEEE-754 format
1213
1214 |  |  |  | Trip coil 1 current flow | 32-bit floating point, IEEE-754 format
1215
1216 |  |  |  | Trip coil 2 peak current | 32-bit floating point, IEEE-754 format
1217
1218 |  |  |  | Trip coil 2 current flow | 32-bit floating point, IEEE-754 format
1219
1220 |  |  |  | Close coil peak current | 32-bit floating point, IEEE-754 format
1221
1222 |  |  |  | Close coil current flow | 32-bit floating point, IEEE-754 format
1223
1224 |  |  |  | A Contact operating time | 32-bit floating point, IEEE-754 format
1225
1226 |  |  |  | B Contact operating time | 32-bit floating point, IEEE-754 format
1227
1228 |  |  |  | A Phase shut-off/make time | 32-bit floating point, IEEE-754 format
1229
1230 |  |  |  | B Phase shut-off/make time | 32-bit floating point, IEEE-754 format
1231
1232 |  |  |  | C Phase shut-off/make time | 32-bit floating point, IEEE-754 format
1233

## 차단기동작파형
Register | Function code | Permissions | Group size | Description |  | Data format | Register | Function code | Permissions | Group size | Description |  | Data format | Register | Function code | Permissions | Group size | Description |  | Data format | Register | Function code | Permissions | Group size | Description |  | Data format | Register | Function code | Permissions | Group size | Description |  | Data format | Register | Function code | Permissions | Group size | Description |  | Data format | Register | Function code | Permissions | Group size | Description |  | Data format | Register | Function code | Permissions | Group size | Description |  |  |  | Data format
1300 | 0x03 | R | 64 | Trip coil 1 전류 # | 1 | 16-bit unsigned integer | 3604 | 0x03 | R | 64 | Trip coil 2 전류 # | 1 | 16-bit unsigned integer | 5908 | 0x03 | R | 64 | Close coil 전류 # | 1 | 16-bit unsigned integer | 8212 | 0x03 | R | 64 | 전압 # | 1 | 16-bit signed integer | 10516 | 0x03 | R | 64 | A상 전류 # | 1 | 16-bit signed integer | 12820 | 0x03 | R | 64 | B상 전류 # | 1 | 16-bit signed integer | 15124 | 0x03 | R | 64 | C상 전류 # | 1 | 16-bit signed integer | 17428 | 0x03 | R | 64 | InitiateAndContact # | 1 | , # | 2 | 16-bit signed integer
1301 |  |  |  | Trip coil 1 전류 # | 2 |  | 3605 |  |  |  | Trip coil 2 전류 # | 2 |  | 5909 |  |  |  | Close coil 전류 # | 2 |  | 8213 |  |  |  | 전압 # | 2 |  | 10517 |  |  |  | A상 전류 # | 2 |  | 12821 |  |  |  | B상 전류 # | 2 |  | 15125 |  |  |  | C상 전류 # | 2 |  | 17429 |  |  |  | InitiateAndContact # | 3 | , # | 4
1302 |  |  |  | Trip coil 1 전류 # | 3 |  | 3606 |  |  |  | Trip coil 2 전류 # | 3 |  | 5910 |  |  |  | Close coil 전류 # | 3 |  | 8214 |  |  |  | 전압 # | 3 |  | 10518 |  |  |  | A상 전류 # | 3 |  | 12822 |  |  |  | B상 전류 # | 3 |  | 15126 |  |  |  | C상 전류 # | 3 |  | 17430 |  |  |  | InitiateAndContact # | 5 | , # | 6
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
1361 |  |  |  | Trip coil 1 전류 # | 62 |  | 3665 |  |  |  | Trip coil 2 전류 # | 62 |  | 5969 |  |  |  | Close coil 전류 # | 62 |  | 8273 |  |  |  | 전압 # | 62 |  | 10577 |  |  |  | A상 전류 # | 62 |  | 12881 |  |  |  | B상 전류 # | 62 |  | 15185 |  |  |  | C상 전류 # | 62 |  | 17489 |  |  |  | InitiateAndContact # | 123 | , # | 124
1362 |  |  |  | Trip coil 1 전류 # | 63 |  | 3666 |  |  |  | Trip coil 2 전류 # | 63 |  | 5970 |  |  |  | Close coil 전류 # | 63 |  | 8274 |  |  |  | 전압 # | 63 |  | 10578 |  |  |  | A상 전류 # | 63 |  | 12882 |  |  |  | B상 전류 # | 63 |  | 15186 |  |  |  | C상 전류 # | 63 |  | 17490 |  |  |  | InitiateAndContact # | 125 | , # | 126
1363 |  |  |  | Trip coil 1 전류 # | 64 |  | 3667 |  |  |  | Trip coil 2 전류 # | 64 |  | 5971 |  |  |  | Close coil 전류 # | 64 |  | 8275 |  |  |  | 전압 # | 64 |  | 10579 |  |  |  | A상 전류 # | 64 |  | 12883 |  |  |  | B상 전류 # | 64 |  | 15187 |  |  |  | C상 전류 # | 64 |  | 17491 |  |  |  | InitiateAndContact # | 127 | , # | 128
1364 | 0x03 | R | 64 | Trip coil 1 전류 # | 65 | 16-bit unsigned integer | 3668 | 0x03 | R | 64 | Trip coil 2 전류 # | 65 | 16-bit unsigned integer | 5972 | 0x03 | R | 64 | Close coil 전류 # | 65 | 16-bit unsigned integer | 8276 | 0x03 | R | 64 | 전압 # | 65 | 16-bit signed integer | 10580 | 0x03 | R | 64 | A상 전류 # | 65 | 16-bit signed integer | 12884 | 0x03 | R | 64 | B상 전류 # | 65 | 16-bit signed integer | 15188 | 0x03 | R | 64 | C상 전류 # | 65 | 16-bit signed integer | 17492 | 0x03 | R | 64 | InitiateAndContact # | 129 | , # | 130 | 16-bit signed integer
1365 |  |  |  | Trip coil 1 전류 # | 66 |  | 3669 |  |  |  | Trip coil 2 전류 # | 66 |  | 5973 |  |  |  | Close coil 전류 # | 66 |  | 8277 |  |  |  | 전압 # | 66 |  | 10581 |  |  |  | A상 전류 # | 66 |  | 12885 |  |  |  | B상 전류 # | 66 |  | 15189 |  |  |  | C상 전류 # | 66 |  | 17493 |  |  |  | InitiateAndContact # | 131 | , # | 132
1366 |  |  |  | Trip coil 1 전류 # | 67 |  | 3670 |  |  |  | Trip coil 2 전류 # | 67 |  | 5974 |  |  |  | Close coil 전류 # | 67 |  | 8278 |  |  |  | 전압 # | 67 |  | 10582 |  |  |  | A상 전류 # | 67 |  | 12886 |  |  |  | B상 전류 # | 67 |  | 15190 |  |  |  | C상 전류 # | 67 |  | 17494 |  |  |  | InitiateAndContact # | 133 | , # | 134
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
1425 |  |  |  | Trip coil 1 전류 # | 126 |  | 3729 |  |  |  | Trip coil 2 전류 # | 126 |  | 6033 |  |  |  | Close coil 전류 # | 126 |  | 8337 |  |  |  | 전압 # | 126 |  | 10641 |  |  |  | A상 전류 # | 126 |  | 12945 |  |  |  | B상 전류 # | 126 |  | 15249 |  |  |  | C상 전류 # | 126 |  | 17553 |  |  |  | InitiateAndContact # | 251 | , # | 252
1426 |  |  |  | Trip coil 1 전류 # | 127 |  | 3730 |  |  |  | Trip coil 2 전류 # | 127 |  | 6034 |  |  |  | Close coil 전류 # | 127 |  | 8338 |  |  |  | 전압 # | 127 |  | 10642 |  |  |  | A상 전류 # | 127 |  | 12946 |  |  |  | B상 전류 # | 127 |  | 15250 |  |  |  | C상 전류 # | 127 |  | 17554 |  |  |  | InitiateAndContact # | 253 | , # | 254
1427 |  |  |  | Trip coil 1 전류 # | 128 |  | 3731 |  |  |  | Trip coil 2 전류 # | 128 |  | 6035 |  |  |  | Close coil 전류 # | 128 |  | 8339 |  |  |  | 전압 # | 128 |  | 10643 |  |  |  | A상 전류 # | 128 |  | 12947 |  |  |  | B상 전류 # | 128 |  | 15251 |  |  |  | C상 전류 # | 128 |  | 17555 |  |  |  | InitiateAndContact # | 255 | , # | 256
1428 | 0x03 | R | 64 | Trip coil 1 전류 # | 129 | 16-bit unsigned integer | 3732 | 0x03 | R | 64 | Trip coil 2 전류 # | 129 | 16-bit unsigned integer | 6036 | 0x03 | R | 64 | Close coil 전류 # | 129 | 16-bit unsigned integer | 8340 | 0x03 | R | 64 | 전압 # | 129 | 16-bit signed integer | 10644 | 0x03 | R | 64 | A상 전류 # | 129 | 16-bit signed integer | 12948 | 0x03 | R | 64 | B상 전류 # | 129 | 16-bit signed integer | 15252 | 0x03 | R | 64 | C상 전류 # | 129 | 16-bit signed integer | 17556 | 0x03 | R | 64 | InitiateAndContact # | 257 | , # | 258 | 16-bit signed integer
1429 |  |  |  | Trip coil 1 전류 # | 130 |  | 3733 |  |  |  | Trip coil 2 전류 # | 130 |  | 6037 |  |  |  | Close coil 전류 # | 130 |  | 8341 |  |  |  | 전압 # | 130 |  | 10645 |  |  |  | A상 전류 # | 130 |  | 12949 |  |  |  | B상 전류 # | 130 |  | 15253 |  |  |  | C상 전류 # | 130 |  | 17557 |  |  |  | InitiateAndContact # | 259 | , # | 260
1430 |  |  |  | Trip coil 1 전류 # | 131 |  | 3734 |  |  |  | Trip coil 2 전류 # | 131 |  | 6038 |  |  |  | Close coil 전류 # | 131 |  | 8342 |  |  |  | 전압 # | 131 |  | 10646 |  |  |  | A상 전류 # | 131 |  | 12950 |  |  |  | B상 전류 # | 131 |  | 15254 |  |  |  | C상 전류 # | 131 |  | 17558 |  |  |  | InitiateAndContact # | 261 | , # | 262
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
1489 |  |  |  | Trip coil 1 전류 # | 190 |  | 3793 |  |  |  | Trip coil 2 전류 # | 190 |  | 6097 |  |  |  | Close coil 전류 # | 190 |  | 8401 |  |  |  | 전압 # | 190 |  | 10705 |  |  |  | A상 전류 # | 190 |  | 13009 |  |  |  | B상 전류 # | 190 |  | 15313 |  |  |  | C상 전류 # | 190 |  | 17617 |  |  |  | InitiateAndContact # | 379 | , # | 380
1490 |  |  |  | Trip coil 1 전류 # | 191 |  | 3794 |  |  |  | Trip coil 2 전류 # | 191 |  | 6098 |  |  |  | Close coil 전류 # | 191 |  | 8402 |  |  |  | 전압 # | 191 |  | 10706 |  |  |  | A상 전류 # | 191 |  | 13010 |  |  |  | B상 전류 # | 191 |  | 15314 |  |  |  | C상 전류 # | 191 |  | 17618 |  |  |  | InitiateAndContact # | 381 | , # | 382
1491 |  |  |  | Trip coil 1 전류 # | 192 |  | 3795 |  |  |  | Trip coil 2 전류 # | 192 |  | 6099 |  |  |  | Close coil 전류 # | 192 |  | 8403 |  |  |  | 전압 # | 192 |  | 10707 |  |  |  | A상 전류 # | 192 |  | 13011 |  |  |  | B상 전류 # | 192 |  | 15315 |  |  |  | C상 전류 # | 192 |  | 17619 |  |  |  | InitiateAndContact # | 383 | , # | 384
1492 | 0x03 | R | 64 | Trip coil 1 전류 # | 193 | 16-bit unsigned integer | 3796 | 0x03 | R | 64 | Trip coil 2 전류 # | 193 | 16-bit unsigned integer | 6100 | 0x03 | R | 64 | Close coil 전류 # | 193 | 16-bit unsigned integer | 8404 | 0x03 | R | 64 | 전압 # | 193 | 16-bit signed integer | 10708 | 0x03 | R | 64 | A상 전류 # | 193 | 16-bit signed integer | 13012 | 0x03 | R | 64 | B상 전류 # | 193 | 16-bit signed integer | 15316 | 0x03 | R | 64 | C상 전류 # | 193 | 16-bit signed integer | 17620 | 0x03 | R | 64 | InitiateAndContact # | 385 | , # | 386 | 16-bit signed integer
1493 |  |  |  | Trip coil 1 전류 # | 194 |  | 3797 |  |  |  | Trip coil 2 전류 # | 194 |  | 6101 |  |  |  | Close coil 전류 # | 194 |  | 8405 |  |  |  | 전압 # | 194 |  | 10709 |  |  |  | A상 전류 # | 194 |  | 13013 |  |  |  | B상 전류 # | 194 |  | 15317 |  |  |  | C상 전류 # | 194 |  | 17621 |  |  |  | InitiateAndContact # | 387 | , # | 388
1494 |  |  |  | Trip coil 1 전류 # | 195 |  | 3798 |  |  |  | Trip coil 2 전류 # | 195 |  | 6102 |  |  |  | Close coil 전류 # | 195 |  | 8406 |  |  |  | 전압 # | 195 |  | 10710 |  |  |  | A상 전류 # | 195 |  | 13014 |  |  |  | B상 전류 # | 195 |  | 15318 |  |  |  | C상 전류 # | 195 |  | 17622 |  |  |  | InitiateAndContact # | 389 | , # | 390
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
1553 |  |  |  | Trip coil 1 전류 # | 254 |  | 3857 |  |  |  | Trip coil 2 전류 # | 254 |  | 6161 |  |  |  | Close coil 전류 # | 254 |  | 8465 |  |  |  | 전압 # | 254 |  | 10769 |  |  |  | A상 전류 # | 254 |  | 13073 |  |  |  | B상 전류 # | 254 |  | 15377 |  |  |  | C상 전류 # | 254 |  | 17681 |  |  |  | InitiateAndContact # | 507 | , # | 508
1554 |  |  |  | Trip coil 1 전류 # | 255 |  | 3858 |  |  |  | Trip coil 2 전류 # | 255 |  | 6162 |  |  |  | Close coil 전류 # | 255 |  | 8466 |  |  |  | 전압 # | 255 |  | 10770 |  |  |  | A상 전류 # | 255 |  | 13074 |  |  |  | B상 전류 # | 255 |  | 15378 |  |  |  | C상 전류 # | 255 |  | 17682 |  |  |  | InitiateAndContact # | 509 | , # | 510
1555 |  |  |  | Trip coil 1 전류 # | 256 |  | 3859 |  |  |  | Trip coil 2 전류 # | 256 |  | 6163 |  |  |  | Close coil 전류 # | 256 |  | 8467 |  |  |  | 전압 # | 256 |  | 10771 |  |  |  | A상 전류 # | 256 |  | 13075 |  |  |  | B상 전류 # | 256 |  | 15379 |  |  |  | C상 전류 # | 256 |  | 17683 |  |  |  | InitiateAndContact # | 511 | , # | 512
1556 | 0x03 | R | 64 | Trip coil 1 전류 # | 257 | 16-bit unsigned integer | 3860 | 0x03 | R | 64 | Trip coil 2 전류 # | 257 | 16-bit unsigned integer | 6164 | 0x03 | R | 64 | Close coil 전류 # | 257 | 16-bit unsigned integer | 8468 | 0x03 | R | 64 | 전압 # | 257 | 16-bit signed integer | 10772 | 0x03 | R | 64 | A상 전류 # | 257 | 16-bit signed integer | 13076 | 0x03 | R | 64 | B상 전류 # | 257 | 16-bit signed integer | 15380 | 0x03 | R | 64 | C상 전류 # | 257 | 16-bit signed integer | 17684 | 0x03 | R | 64 | InitiateAndContact # | 513 | , # | 514 | 16-bit signed integer
1557 |  |  |  | Trip coil 1 전류 # | 258 |  | 3861 |  |  |  | Trip coil 2 전류 # | 258 |  | 6165 |  |  |  | Close coil 전류 # | 258 |  | 8469 |  |  |  | 전압 # | 258 |  | 10773 |  |  |  | A상 전류 # | 258 |  | 13077 |  |  |  | B상 전류 # | 258 |  | 15381 |  |  |  | C상 전류 # | 258 |  | 17685 |  |  |  | InitiateAndContact # | 515 | , # | 516
1558 |  |  |  | Trip coil 1 전류 # | 259 |  | 3862 |  |  |  | Trip coil 2 전류 # | 259 |  | 6166 |  |  |  | Close coil 전류 # | 259 |  | 8470 |  |  |  | 전압 # | 259 |  | 10774 |  |  |  | A상 전류 # | 259 |  | 13078 |  |  |  | B상 전류 # | 259 |  | 15382 |  |  |  | C상 전류 # | 259 |  | 17686 |  |  |  | InitiateAndContact # | 517 | , # | 518
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
1617 |  |  |  | Trip coil 1 전류 # | 318 |  | 3921 |  |  |  | Trip coil 2 전류 # | 318 |  | 6225 |  |  |  | Close coil 전류 # | 318 |  | 8529 |  |  |  | 전압 # | 318 |  | 10833 |  |  |  | A상 전류 # | 318 |  | 13137 |  |  |  | B상 전류 # | 318 |  | 15441 |  |  |  | C상 전류 # | 318 |  | 17745 |  |  |  | InitiateAndContact # | 635 | , # | 636
1618 |  |  |  | Trip coil 1 전류 # | 319 |  | 3922 |  |  |  | Trip coil 2 전류 # | 319 |  | 6226 |  |  |  | Close coil 전류 # | 319 |  | 8530 |  |  |  | 전압 # | 319 |  | 10834 |  |  |  | A상 전류 # | 319 |  | 13138 |  |  |  | B상 전류 # | 319 |  | 15442 |  |  |  | C상 전류 # | 319 |  | 17746 |  |  |  | InitiateAndContact # | 637 | , # | 638
1619 |  |  |  | Trip coil 1 전류 # | 320 |  | 3923 |  |  |  | Trip coil 2 전류 # | 320 |  | 6227 |  |  |  | Close coil 전류 # | 320 |  | 8531 |  |  |  | 전압 # | 320 |  | 10835 |  |  |  | A상 전류 # | 320 |  | 13139 |  |  |  | B상 전류 # | 320 |  | 15443 |  |  |  | C상 전류 # | 320 |  | 17747 |  |  |  | InitiateAndContact # | 639 | , # | 640
1620 | 0x03 | R | 64 | Trip coil 1 전류 # | 321 | 16-bit unsigned integer | 3924 | 0x03 | R | 64 | Trip coil 2 전류 # | 321 | 16-bit unsigned integer | 6228 | 0x03 | R | 64 | Close coil 전류 # | 321 | 16-bit unsigned integer | 8532 | 0x03 | R | 64 | 전압 # | 321 | 16-bit signed integer | 10836 | 0x03 | R | 64 | A상 전류 # | 321 | 16-bit signed integer | 13140 | 0x03 | R | 64 | B상 전류 # | 321 | 16-bit signed integer | 15444 | 0x03 | R | 64 | C상 전류 # | 321 | 16-bit signed integer | 17748 | 0x03 | R | 64 | InitiateAndContact # | 641 | , # | 642 | 16-bit signed integer
1621 |  |  |  | Trip coil 1 전류 # | 322 |  | 3925 |  |  |  | Trip coil 2 전류 # | 322 |  | 6229 |  |  |  | Close coil 전류 # | 322 |  | 8533 |  |  |  | 전압 # | 322 |  | 10837 |  |  |  | A상 전류 # | 322 |  | 13141 |  |  |  | B상 전류 # | 322 |  | 15445 |  |  |  | C상 전류 # | 322 |  | 17749 |  |  |  | InitiateAndContact # | 643 | , # | 644
1622 |  |  |  | Trip coil 1 전류 # | 323 |  | 3926 |  |  |  | Trip coil 2 전류 # | 323 |  | 6230 |  |  |  | Close coil 전류 # | 323 |  | 8534 |  |  |  | 전압 # | 323 |  | 10838 |  |  |  | A상 전류 # | 323 |  | 13142 |  |  |  | B상 전류 # | 323 |  | 15446 |  |  |  | C상 전류 # | 323 |  | 17750 |  |  |  | InitiateAndContact # | 645 | , # | 646
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
1681 |  |  |  | Trip coil 1 전류 # | 382 |  | 3985 |  |  |  | Trip coil 2 전류 # | 382 |  | 6289 |  |  |  | Close coil 전류 # | 382 |  | 8593 |  |  |  | 전압 # | 382 |  | 10897 |  |  |  | A상 전류 # | 382 |  | 13201 |  |  |  | B상 전류 # | 382 |  | 15505 |  |  |  | C상 전류 # | 382 |  | 17809 |  |  |  | InitiateAndContact # | 763 | , # | 764
1682 |  |  |  | Trip coil 1 전류 # | 383 |  | 3986 |  |  |  | Trip coil 2 전류 # | 383 |  | 6290 |  |  |  | Close coil 전류 # | 383 |  | 8594 |  |  |  | 전압 # | 383 |  | 10898 |  |  |  | A상 전류 # | 383 |  | 13202 |  |  |  | B상 전류 # | 383 |  | 15506 |  |  |  | C상 전류 # | 383 |  | 17810 |  |  |  | InitiateAndContact # | 765 | , # | 766
1683 |  |  |  | Trip coil 1 전류 # | 384 |  | 3987 |  |  |  | Trip coil 2 전류 # | 384 |  | 6291 |  |  |  | Close coil 전류 # | 384 |  | 8595 |  |  |  | 전압 # | 384 |  | 10899 |  |  |  | A상 전류 # | 384 |  | 13203 |  |  |  | B상 전류 # | 384 |  | 15507 |  |  |  | C상 전류 # | 384 |  | 17811 |  |  |  | InitiateAndContact # | 767 | , # | 768
1684 | 0x03 | R | 64 | Trip coil 1 전류 # | 385 | 16-bit unsigned integer | 3988 | 0x03 | R | 64 | Trip coil 2 전류 # | 385 | 16-bit unsigned integer | 6292 | 0x03 | R | 64 | Close coil 전류 # | 385 | 16-bit unsigned integer | 8596 | 0x03 | R | 64 | 전압 # | 385 | 16-bit signed integer | 10900 | 0x03 | R | 64 | A상 전류 # | 385 | 16-bit signed integer | 13204 | 0x03 | R | 64 | B상 전류 # | 385 | 16-bit signed integer | 15508 | 0x03 | R | 64 | C상 전류 # | 385 | 16-bit signed integer | 17812 | 0x03 | R | 64 | InitiateAndContact # | 769 | , # | 770 | 16-bit signed integer
1685 |  |  |  | Trip coil 1 전류 # | 386 |  | 3989 |  |  |  | Trip coil 2 전류 # | 386 |  | 6293 |  |  |  | Close coil 전류 # | 386 |  | 8597 |  |  |  | 전압 # | 386 |  | 10901 |  |  |  | A상 전류 # | 386 |  | 13205 |  |  |  | B상 전류 # | 386 |  | 15509 |  |  |  | C상 전류 # | 386 |  | 17813 |  |  |  | InitiateAndContact # | 771 | , # | 772
1686 |  |  |  | Trip coil 1 전류 # | 387 |  | 3990 |  |  |  | Trip coil 2 전류 # | 387 |  | 6294 |  |  |  | Close coil 전류 # | 387 |  | 8598 |  |  |  | 전압 # | 387 |  | 10902 |  |  |  | A상 전류 # | 387 |  | 13206 |  |  |  | B상 전류 # | 387 |  | 15510 |  |  |  | C상 전류 # | 387 |  | 17814 |  |  |  | InitiateAndContact # | 773 | , # | 774
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
1745 |  |  |  | Trip coil 1 전류 # | 446 |  | 4049 |  |  |  | Trip coil 2 전류 # | 446 |  | 6353 |  |  |  | Close coil 전류 # | 446 |  | 8657 |  |  |  | 전압 # | 446 |  | 10961 |  |  |  | A상 전류 # | 446 |  | 13265 |  |  |  | B상 전류 # | 446 |  | 15569 |  |  |  | C상 전류 # | 446 |  | 17873 |  |  |  | InitiateAndContact # | 891 | , # | 892
1746 |  |  |  | Trip coil 1 전류 # | 447 |  | 4050 |  |  |  | Trip coil 2 전류 # | 447 |  | 6354 |  |  |  | Close coil 전류 # | 447 |  | 8658 |  |  |  | 전압 # | 447 |  | 10962 |  |  |  | A상 전류 # | 447 |  | 13266 |  |  |  | B상 전류 # | 447 |  | 15570 |  |  |  | C상 전류 # | 447 |  | 17874 |  |  |  | InitiateAndContact # | 893 | , # | 894
1747 |  |  |  | Trip coil 1 전류 # | 448 |  | 4051 |  |  |  | Trip coil 2 전류 # | 448 |  | 6355 |  |  |  | Close coil 전류 # | 448 |  | 8659 |  |  |  | 전압 # | 448 |  | 10963 |  |  |  | A상 전류 # | 448 |  | 13267 |  |  |  | B상 전류 # | 448 |  | 15571 |  |  |  | C상 전류 # | 448 |  | 17875 |  |  |  | InitiateAndContact # | 895 | , # | 896
1748 | 0x03 | R | 64 | Trip coil 1 전류 # | 449 | 16-bit unsigned integer | 4052 | 0x03 | R | 64 | Trip coil 2 전류 # | 449 | 16-bit unsigned integer | 6356 | 0x03 | R | 64 | Close coil 전류 # | 449 | 16-bit unsigned integer | 8660 | 0x03 | R | 64 | 전압 # | 449 | 16-bit signed integer | 10964 | 0x03 | R | 64 | A상 전류 # | 449 | 16-bit signed integer | 13268 | 0x03 | R | 64 | B상 전류 # | 449 | 16-bit signed integer | 15572 | 0x03 | R | 64 | C상 전류 # | 449 | 16-bit signed integer | 17876 | 0x03 | R | 64 | InitiateAndContact # | 897 | , # | 898 | 16-bit signed integer
1749 |  |  |  | Trip coil 1 전류 # | 450 |  | 4053 |  |  |  | Trip coil 2 전류 # | 450 |  | 6357 |  |  |  | Close coil 전류 # | 450 |  | 8661 |  |  |  | 전압 # | 450 |  | 10965 |  |  |  | A상 전류 # | 450 |  | 13269 |  |  |  | B상 전류 # | 450 |  | 15573 |  |  |  | C상 전류 # | 450 |  | 17877 |  |  |  | InitiateAndContact # | 899 | , # | 900
1750 |  |  |  | Trip coil 1 전류 # | 451 |  | 4054 |  |  |  | Trip coil 2 전류 # | 451 |  | 6358 |  |  |  | Close coil 전류 # | 451 |  | 8662 |  |  |  | 전압 # | 451 |  | 10966 |  |  |  | A상 전류 # | 451 |  | 13270 |  |  |  | B상 전류 # | 451 |  | 15574 |  |  |  | C상 전류 # | 451 |  | 17878 |  |  |  | InitiateAndContact # | 901 | , # | 902
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
1809 |  |  |  | Trip coil 1 전류 # | 510 |  | 4113 |  |  |  | Trip coil 2 전류 # | 510 |  | 6417 |  |  |  | Close coil 전류 # | 510 |  | 8721 |  |  |  | 전압 # | 510 |  | 11025 |  |  |  | A상 전류 # | 510 |  | 13329 |  |  |  | B상 전류 # | 510 |  | 15633 |  |  |  | C상 전류 # | 510 |  | 17937 |  |  |  | InitiateAndContact # | 1019 | , # | 1020
1810 |  |  |  | Trip coil 1 전류 # | 511 |  | 4114 |  |  |  | Trip coil 2 전류 # | 511 |  | 6418 |  |  |  | Close coil 전류 # | 511 |  | 8722 |  |  |  | 전압 # | 511 |  | 11026 |  |  |  | A상 전류 # | 511 |  | 13330 |  |  |  | B상 전류 # | 511 |  | 15634 |  |  |  | C상 전류 # | 511 |  | 17938 |  |  |  | InitiateAndContact # | 1021 | , # | 1022
1811 |  |  |  | Trip coil 1 전류 # | 512 |  | 4115 |  |  |  | Trip coil 2 전류 # | 512 |  | 6419 |  |  |  | Close coil 전류 # | 512 |  | 8723 |  |  |  | 전압 # | 512 |  | 11027 |  |  |  | A상 전류 # | 512 |  | 13331 |  |  |  | B상 전류 # | 512 |  | 15635 |  |  |  | C상 전류 # | 512 |  | 17939 |  |  |  | InitiateAndContact # | 1023 | , # | 1024
1812 | 0x03 | R | 64 | Trip coil 1 전류 # | 513 | 16-bit unsigned integer | 4116 | 0x03 | R | 64 | Trip coil 2 전류 # | 513 | 16-bit unsigned integer | 6420 | 0x03 | R | 64 | Close coil 전류 # | 513 | 16-bit unsigned integer | 8724 | 0x03 | R | 64 | 전압 # | 513 | 16-bit signed integer | 11028 | 0x03 | R | 64 | A상 전류 # | 513 | 16-bit signed integer | 13332 | 0x03 | R | 64 | B상 전류 # | 513 | 16-bit signed integer | 15636 | 0x03 | R | 64 | C상 전류 # | 513 | 16-bit signed integer | 17940 | 0x03 | R | 64 | InitiateAndContact # | 1025 | , # | 1026 | 16-bit signed integer
1813 |  |  |  | Trip coil 1 전류 # | 514 |  | 4117 |  |  |  | Trip coil 2 전류 # | 514 |  | 6421 |  |  |  | Close coil 전류 # | 514 |  | 8725 |  |  |  | 전압 # | 514 |  | 11029 |  |  |  | A상 전류 # | 514 |  | 13333 |  |  |  | B상 전류 # | 514 |  | 15637 |  |  |  | C상 전류 # | 514 |  | 17941 |  |  |  | InitiateAndContact # | 1027 | , # | 1028
1814 |  |  |  | Trip coil 1 전류 # | 515 |  | 4118 |  |  |  | Trip coil 2 전류 # | 515 |  | 6422 |  |  |  | Close coil 전류 # | 515 |  | 8726 |  |  |  | 전압 # | 515 |  | 11030 |  |  |  | A상 전류 # | 515 |  | 13334 |  |  |  | B상 전류 # | 515 |  | 15638 |  |  |  | C상 전류 # | 515 |  | 17942 |  |  |  | InitiateAndContact # | 1029 | , # | 1030
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
1873 |  |  |  | Trip coil 1 전류 # | 574 |  | 4177 |  |  |  | Trip coil 2 전류 # | 574 |  | 6481 |  |  |  | Close coil 전류 # | 574 |  | 8785 |  |  |  | 전압 # | 574 |  | 11089 |  |  |  | A상 전류 # | 574 |  | 13393 |  |  |  | B상 전류 # | 574 |  | 15697 |  |  |  | C상 전류 # | 574 |  | 18001 |  |  |  | InitiateAndContact # | 1147 | , # | 1148
1874 |  |  |  | Trip coil 1 전류 # | 575 |  | 4178 |  |  |  | Trip coil 2 전류 # | 575 |  | 6482 |  |  |  | Close coil 전류 # | 575 |  | 8786 |  |  |  | 전압 # | 575 |  | 11090 |  |  |  | A상 전류 # | 575 |  | 13394 |  |  |  | B상 전류 # | 575 |  | 15698 |  |  |  | C상 전류 # | 575 |  | 18002 |  |  |  | InitiateAndContact # | 1149 | , # | 1150
1875 |  |  |  | Trip coil 1 전류 # | 576 |  | 4179 |  |  |  | Trip coil 2 전류 # | 576 |  | 6483 |  |  |  | Close coil 전류 # | 576 |  | 8787 |  |  |  | 전압 # | 576 |  | 11091 |  |  |  | A상 전류 # | 576 |  | 13395 |  |  |  | B상 전류 # | 576 |  | 15699 |  |  |  | C상 전류 # | 576 |  | 18003 |  |  |  | InitiateAndContact # | 1151 | , # | 1152
1876 | 0x03 | R | 64 | Trip coil 1 전류 # | 577 | 16-bit unsigned integer | 4180 | 0x03 | R | 64 | Trip coil 2 전류 # | 577 | 16-bit unsigned integer | 6484 | 0x03 | R | 64 | Close coil 전류 # | 577 | 16-bit unsigned integer | 8788 | 0x03 | R | 64 | 전압 # | 577 | 16-bit signed integer | 11092 | 0x03 | R | 64 | A상 전류 # | 577 | 16-bit signed integer | 13396 | 0x03 | R | 64 | B상 전류 # | 577 | 16-bit signed integer | 15700 | 0x03 | R | 64 | C상 전류 # | 577 | 16-bit signed integer | 18004 | 0x03 | R | 64 | InitiateAndContact # | 1153 | , # | 1154 | 16-bit signed integer
1877 |  |  |  | Trip coil 1 전류 # | 578 |  | 4181 |  |  |  | Trip coil 2 전류 # | 578 |  | 6485 |  |  |  | Close coil 전류 # | 578 |  | 8789 |  |  |  | 전압 # | 578 |  | 11093 |  |  |  | A상 전류 # | 578 |  | 13397 |  |  |  | B상 전류 # | 578 |  | 15701 |  |  |  | C상 전류 # | 578 |  | 18005 |  |  |  | InitiateAndContact # | 1155 | , # | 1156
1878 |  |  |  | Trip coil 1 전류 # | 579 |  | 4182 |  |  |  | Trip coil 2 전류 # | 579 |  | 6486 |  |  |  | Close coil 전류 # | 579 |  | 8790 |  |  |  | 전압 # | 579 |  | 11094 |  |  |  | A상 전류 # | 579 |  | 13398 |  |  |  | B상 전류 # | 579 |  | 15702 |  |  |  | C상 전류 # | 579 |  | 18006 |  |  |  | InitiateAndContact # | 1157 | , # | 1158
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
1937 |  |  |  | Trip coil 1 전류 # | 638 |  | 4241 |  |  |  | Trip coil 2 전류 # | 638 |  | 6545 |  |  |  | Close coil 전류 # | 638 |  | 8849 |  |  |  | 전압 # | 638 |  | 11153 |  |  |  | A상 전류 # | 638 |  | 13457 |  |  |  | B상 전류 # | 638 |  | 15761 |  |  |  | C상 전류 # | 638 |  | 18065 |  |  |  | InitiateAndContact # | 1275 | , # | 1276
1938 |  |  |  | Trip coil 1 전류 # | 639 |  | 4242 |  |  |  | Trip coil 2 전류 # | 639 |  | 6546 |  |  |  | Close coil 전류 # | 639 |  | 8850 |  |  |  | 전압 # | 639 |  | 11154 |  |  |  | A상 전류 # | 639 |  | 13458 |  |  |  | B상 전류 # | 639 |  | 15762 |  |  |  | C상 전류 # | 639 |  | 18066 |  |  |  | InitiateAndContact # | 1277 | , # | 1278
1939 |  |  |  | Trip coil 1 전류 # | 640 |  | 4243 |  |  |  | Trip coil 2 전류 # | 640 |  | 6547 |  |  |  | Close coil 전류 # | 640 |  | 8851 |  |  |  | 전압 # | 640 |  | 11155 |  |  |  | A상 전류 # | 640 |  | 13459 |  |  |  | B상 전류 # | 640 |  | 15763 |  |  |  | C상 전류 # | 640 |  | 18067 |  |  |  | InitiateAndContact # | 1279 | , # | 1280
1940 | 0x03 | R | 64 | Trip coil 1 전류 # | 641 | 16-bit unsigned integer | 4244 | 0x03 | R | 64 | Trip coil 2 전류 # | 641 | 16-bit unsigned integer | 6548 | 0x03 | R | 64 | Close coil 전류 # | 641 | 16-bit unsigned integer | 8852 | 0x03 | R | 64 | 전압 # | 641 | 16-bit signed integer | 11156 | 0x03 | R | 64 | A상 전류 # | 641 | 16-bit signed integer | 13460 | 0x03 | R | 64 | B상 전류 # | 641 | 16-bit signed integer | 15764 | 0x03 | R | 64 | C상 전류 # | 641 | 16-bit signed integer | 18068 | 0x03 | R | 64 | InitiateAndContact # | 1281 | , # | 1282 | 16-bit signed integer
1941 |  |  |  | Trip coil 1 전류 # | 642 |  | 4245 |  |  |  | Trip coil 2 전류 # | 642 |  | 6549 |  |  |  | Close coil 전류 # | 642 |  | 8853 |  |  |  | 전압 # | 642 |  | 11157 |  |  |  | A상 전류 # | 642 |  | 13461 |  |  |  | B상 전류 # | 642 |  | 15765 |  |  |  | C상 전류 # | 642 |  | 18069 |  |  |  | InitiateAndContact # | 1283 | , # | 1284
1942 |  |  |  | Trip coil 1 전류 # | 643 |  | 4246 |  |  |  | Trip coil 2 전류 # | 643 |  | 6550 |  |  |  | Close coil 전류 # | 643 |  | 8854 |  |  |  | 전압 # | 643 |  | 11158 |  |  |  | A상 전류 # | 643 |  | 13462 |  |  |  | B상 전류 # | 643 |  | 15766 |  |  |  | C상 전류 # | 643 |  | 18070 |  |  |  | InitiateAndContact # | 1285 | , # | 1286
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2001 |  |  |  | Trip coil 1 전류 # | 702 |  | 4305 |  |  |  | Trip coil 2 전류 # | 702 |  | 6609 |  |  |  | Close coil 전류 # | 702 |  | 8913 |  |  |  | 전압 # | 702 |  | 11217 |  |  |  | A상 전류 # | 702 |  | 13521 |  |  |  | B상 전류 # | 702 |  | 15825 |  |  |  | C상 전류 # | 702 |  | 18129 |  |  |  | InitiateAndContact # | 1403 | , # | 1404
2002 |  |  |  | Trip coil 1 전류 # | 703 |  | 4306 |  |  |  | Trip coil 2 전류 # | 703 |  | 6610 |  |  |  | Close coil 전류 # | 703 |  | 8914 |  |  |  | 전압 # | 703 |  | 11218 |  |  |  | A상 전류 # | 703 |  | 13522 |  |  |  | B상 전류 # | 703 |  | 15826 |  |  |  | C상 전류 # | 703 |  | 18130 |  |  |  | InitiateAndContact # | 1405 | , # | 1406
2003 |  |  |  | Trip coil 1 전류 # | 704 |  | 4307 |  |  |  | Trip coil 2 전류 # | 704 |  | 6611 |  |  |  | Close coil 전류 # | 704 |  | 8915 |  |  |  | 전압 # | 704 |  | 11219 |  |  |  | A상 전류 # | 704 |  | 13523 |  |  |  | B상 전류 # | 704 |  | 15827 |  |  |  | C상 전류 # | 704 |  | 18131 |  |  |  | InitiateAndContact # | 1407 | , # | 1408
2004 | 0x03 | R | 64 | Trip coil 1 전류 # | 705 | 16-bit unsigned integer | 4308 | 0x03 | R | 64 | Trip coil 2 전류 # | 705 | 16-bit unsigned integer | 6612 | 0x03 | R | 64 | Close coil 전류 # | 705 | 16-bit unsigned integer | 8916 | 0x03 | R | 64 | 전압 # | 705 | 16-bit signed integer | 11220 | 0x03 | R | 64 | A상 전류 # | 705 | 16-bit signed integer | 13524 | 0x03 | R | 64 | B상 전류 # | 705 | 16-bit signed integer | 15828 | 0x03 | R | 64 | C상 전류 # | 705 | 16-bit signed integer | 18132 | 0x03 | R | 64 | InitiateAndContact # | 1409 | , # | 1410 | 16-bit signed integer
2005 |  |  |  | Trip coil 1 전류 # | 706 |  | 4309 |  |  |  | Trip coil 2 전류 # | 706 |  | 6613 |  |  |  | Close coil 전류 # | 706 |  | 8917 |  |  |  | 전압 # | 706 |  | 11221 |  |  |  | A상 전류 # | 706 |  | 13525 |  |  |  | B상 전류 # | 706 |  | 15829 |  |  |  | C상 전류 # | 706 |  | 18133 |  |  |  | InitiateAndContact # | 1411 | , # | 1412
2006 |  |  |  | Trip coil 1 전류 # | 707 |  | 4310 |  |  |  | Trip coil 2 전류 # | 707 |  | 6614 |  |  |  | Close coil 전류 # | 707 |  | 8918 |  |  |  | 전압 # | 707 |  | 11222 |  |  |  | A상 전류 # | 707 |  | 13526 |  |  |  | B상 전류 # | 707 |  | 15830 |  |  |  | C상 전류 # | 707 |  | 18134 |  |  |  | InitiateAndContact # | 1413 | , # | 1414
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2065 |  |  |  | Trip coil 1 전류 # | 766 |  | 4369 |  |  |  | Trip coil 2 전류 # | 766 |  | 6673 |  |  |  | Close coil 전류 # | 766 |  | 8977 |  |  |  | 전압 # | 766 |  | 11281 |  |  |  | A상 전류 # | 766 |  | 13585 |  |  |  | B상 전류 # | 766 |  | 15889 |  |  |  | C상 전류 # | 766 |  | 18193 |  |  |  | InitiateAndContact # | 1531 | , # | 1532
2066 |  |  |  | Trip coil 1 전류 # | 767 |  | 4370 |  |  |  | Trip coil 2 전류 # | 767 |  | 6674 |  |  |  | Close coil 전류 # | 767 |  | 8978 |  |  |  | 전압 # | 767 |  | 11282 |  |  |  | A상 전류 # | 767 |  | 13586 |  |  |  | B상 전류 # | 767 |  | 15890 |  |  |  | C상 전류 # | 767 |  | 18194 |  |  |  | InitiateAndContact # | 1533 | , # | 1534
2067 |  |  |  | Trip coil 1 전류 # | 768 |  | 4371 |  |  |  | Trip coil 2 전류 # | 768 |  | 6675 |  |  |  | Close coil 전류 # | 768 |  | 8979 |  |  |  | 전압 # | 768 |  | 11283 |  |  |  | A상 전류 # | 768 |  | 13587 |  |  |  | B상 전류 # | 768 |  | 15891 |  |  |  | C상 전류 # | 768 |  | 18195 |  |  |  | InitiateAndContact # | 1535 | , # | 1536
2068 | 0x03 | R | 64 | Trip coil 1 전류 # | 769 | 16-bit unsigned integer | 4372 | 0x03 | R | 64 | Trip coil 2 전류 # | 769 | 16-bit unsigned integer | 6676 | 0x03 | R | 64 | Close coil 전류 # | 769 | 16-bit unsigned integer | 8980 | 0x03 | R | 128 | 전압 # | 769 | 16-bit signed integer | 11284 | 0x03 | R | 128 | A상 전류 # | 769 | 16-bit signed integer | 13588 | 0x03 | R | 128 | B상 전류 # | 769 | 16-bit signed integer | 15892 | 0x03 | R | 64 | C상 전류 # | 769 | 16-bit signed integer | 18196 | 0x03 | R | 64 | InitiateAndContact # | 1537 | , # | 1538 | 16-bit signed integer
2069 |  |  |  | Trip coil 1 전류 # | 770 |  | 4373 |  |  |  | Trip coil 2 전류 # | 770 |  | 6677 |  |  |  | Close coil 전류 # | 770 |  | 8981 |  |  |  | 전압 # | 770 |  | 11285 |  |  |  | A상 전류 # | 770 |  | 13589 |  |  |  | B상 전류 # | 770 |  | 15893 |  |  |  | C상 전류 # | 770 |  | 18197 |  |  |  | InitiateAndContact # | 1539 | , # | 1540
2070 |  |  |  | Trip coil 1 전류 # | 771 |  | 4374 |  |  |  | Trip coil 2 전류 # | 771 |  | 6678 |  |  |  | Close coil 전류 # | 771 |  | 8982 |  |  |  | 전압 # | 771 |  | 11286 |  |  |  | A상 전류 # | 771 |  | 13590 |  |  |  | B상 전류 # | 771 |  | 15894 |  |  |  | C상 전류 # | 771 |  | 18198 |  |  |  | InitiateAndContact # | 1541 | , # | 1542
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2129 |  |  |  | Trip coil 1 전류 # | 830 |  | 4433 |  |  |  | Trip coil 2 전류 # | 830 |  | 6737 |  |  |  | Close coil 전류 # | 830 |  | 9041 |  |  |  | 전압 # | 830 |  | 11345 |  |  |  | A상 전류 # | 830 |  | 13649 |  |  |  | B상 전류 # | 830 |  | 15953 |  |  |  | C상 전류 # | 830 |  | 18257 |  |  |  | InitiateAndContact # | 1659 | , # | 1660
2130 |  |  |  | Trip coil 1 전류 # | 831 |  | 4434 |  |  |  | Trip coil 2 전류 # | 831 |  | 6738 |  |  |  | Close coil 전류 # | 831 |  | 9042 |  |  |  | 전압 # | 831 |  | 11346 |  |  |  | A상 전류 # | 831 |  | 13650 |  |  |  | B상 전류 # | 831 |  | 15954 |  |  |  | C상 전류 # | 831 |  | 18258 |  |  |  | InitiateAndContact # | 1661 | , # | 1662
2131 |  |  |  | Trip coil 1 전류 # | 832 |  | 4435 |  |  |  | Trip coil 2 전류 # | 832 |  | 6739 |  |  |  | Close coil 전류 # | 832 |  | 9043 |  |  |  | 전압 # | 832 |  | 11347 |  |  |  | A상 전류 # | 832 |  | 13651 |  |  |  | B상 전류 # | 832 |  | 15955 |  |  |  | C상 전류 # | 832 |  | 18259 |  |  |  | InitiateAndContact # | 1663 | , # | 1664
2132 | 0x03 | R | 64 | Trip coil 1 전류 # | 833 | 16-bit unsigned integer | 4436 | 0x03 | R | 64 | Trip coil 2 전류 # | 833 | 16-bit unsigned integer | 6740 | 0x03 | R | 64 | Close coil 전류 # | 833 | 16-bit unsigned integer | 9044 | 0x03 | R | 64 | 전압 # | 833 | 16-bit signed integer | 11348 | 0x03 | R | 64 | A상 전류 # | 833 | 16-bit signed integer | 13652 | 0x03 | R | 64 | B상 전류 # | 833 | 16-bit signed integer | 15956 | 0x03 | R | 64 | C상 전류 # | 833 | 16-bit signed integer | 18260 | 0x03 | R | 64 | InitiateAndContact # | 1665 | , # | 1666 | 16-bit signed integer
2133 |  |  |  | Trip coil 1 전류 # | 834 |  | 4437 |  |  |  | Trip coil 2 전류 # | 834 |  | 6741 |  |  |  | Close coil 전류 # | 834 |  | 9045 |  |  |  | 전압 # | 834 |  | 11349 |  |  |  | A상 전류 # | 834 |  | 13653 |  |  |  | B상 전류 # | 834 |  | 15957 |  |  |  | C상 전류 # | 834 |  | 18261 |  |  |  | InitiateAndContact # | 1667 | , # | 1668
2134 |  |  |  | Trip coil 1 전류 # | 835 |  | 4438 |  |  |  | Trip coil 2 전류 # | 835 |  | 6742 |  |  |  | Close coil 전류 # | 835 |  | 9046 |  |  |  | 전압 # | 835 |  | 11350 |  |  |  | A상 전류 # | 835 |  | 13654 |  |  |  | B상 전류 # | 835 |  | 15958 |  |  |  | C상 전류 # | 835 |  | 18262 |  |  |  | InitiateAndContact # | 1669 | , # | 1670
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2193 |  |  |  | Trip coil 1 전류 # | 894 |  | 4497 |  |  |  | Trip coil 2 전류 # | 894 |  | 6801 |  |  |  | Close coil 전류 # | 894 |  | 9105 |  |  |  | 전압 # | 894 |  | 11409 |  |  |  | A상 전류 # | 894 |  | 13713 |  |  |  | B상 전류 # | 894 |  | 16017 |  |  |  | C상 전류 # | 894 |  | 18321 |  |  |  | InitiateAndContact # | 1787 | , # | 1788
2194 |  |  |  | Trip coil 1 전류 # | 895 |  | 4498 |  |  |  | Trip coil 2 전류 # | 895 |  | 6802 |  |  |  | Close coil 전류 # | 895 |  | 9106 |  |  |  | 전압 # | 895 |  | 11410 |  |  |  | A상 전류 # | 895 |  | 13714 |  |  |  | B상 전류 # | 895 |  | 16018 |  |  |  | C상 전류 # | 895 |  | 18322 |  |  |  | InitiateAndContact # | 1789 | , # | 1790
2195 |  |  |  | Trip coil 1 전류 # | 896 |  | 4499 |  |  |  | Trip coil 2 전류 # | 896 |  | 6803 |  |  |  | Close coil 전류 # | 896 |  | 9107 |  |  |  | 전압 # | 896 |  | 11411 |  |  |  | A상 전류 # | 896 |  | 13715 |  |  |  | B상 전류 # | 896 |  | 16019 |  |  |  | C상 전류 # | 896 |  | 18323 |  |  |  | InitiateAndContact # | 1791 | , # | 1792
2196 | 0x03 | R | 64 | Trip coil 1 전류 # | 897 | 16-bit unsigned integer | 4500 | 0x03 | R | 64 | Trip coil 2 전류 # | 897 | 16-bit unsigned integer | 6804 | 0x03 | R | 64 | Close coil 전류 # | 897 | 16-bit unsigned integer | 9108 | 0x03 | R | 64 | 전압 # | 897 | 16-bit signed integer | 11412 | 0x03 | R | 64 | A상 전류 # | 897 | 16-bit signed integer | 13716 | 0x03 | R | 64 | B상 전류 # | 897 | 16-bit signed integer | 16020 | 0x03 | R | 64 | C상 전류 # | 897 | 16-bit signed integer | 18324 | 0x03 | R | 64 | InitiateAndContact # | 1793 | , # | 1794 | 16-bit signed integer
2197 |  |  |  | Trip coil 1 전류 # | 898 |  | 4501 |  |  |  | Trip coil 2 전류 # | 898 |  | 6805 |  |  |  | Close coil 전류 # | 898 |  | 9109 |  |  |  | 전압 # | 898 |  | 11413 |  |  |  | A상 전류 # | 898 |  | 13717 |  |  |  | B상 전류 # | 898 |  | 16021 |  |  |  | C상 전류 # | 898 |  | 18325 |  |  |  | InitiateAndContact # | 1795 | , # | 1796
2198 |  |  |  | Trip coil 1 전류 # | 899 |  | 4502 |  |  |  | Trip coil 2 전류 # | 899 |  | 6806 |  |  |  | Close coil 전류 # | 899 |  | 9110 |  |  |  | 전압 # | 899 |  | 11414 |  |  |  | A상 전류 # | 899 |  | 13718 |  |  |  | B상 전류 # | 899 |  | 16022 |  |  |  | C상 전류 # | 899 |  | 18326 |  |  |  | InitiateAndContact # | 1797 | , # | 1798
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2257 |  |  |  | Trip coil 1 전류 # | 958 |  | 4561 |  |  |  | Trip coil 2 전류 # | 958 |  | 6865 |  |  |  | Close coil 전류 # | 958 |  | 9169 |  |  |  | 전압 # | 958 |  | 11473 |  |  |  | A상 전류 # | 958 |  | 13777 |  |  |  | B상 전류 # | 958 |  | 16081 |  |  |  | C상 전류 # | 958 |  | 18385 |  |  |  | InitiateAndContact # | 1915 | , # | 1916
2258 |  |  |  | Trip coil 1 전류 # | 959 |  | 4562 |  |  |  | Trip coil 2 전류 # | 959 |  | 6866 |  |  |  | Close coil 전류 # | 959 |  | 9170 |  |  |  | 전압 # | 959 |  | 11474 |  |  |  | A상 전류 # | 959 |  | 13778 |  |  |  | B상 전류 # | 959 |  | 16082 |  |  |  | C상 전류 # | 959 |  | 18386 |  |  |  | InitiateAndContact # | 1917 | , # | 1918
2259 |  |  |  | Trip coil 1 전류 # | 960 |  | 4563 |  |  |  | Trip coil 2 전류 # | 960 |  | 6867 |  |  |  | Close coil 전류 # | 960 |  | 9171 |  |  |  | 전압 # | 960 |  | 11475 |  |  |  | A상 전류 # | 960 |  | 13779 |  |  |  | B상 전류 # | 960 |  | 16083 |  |  |  | C상 전류 # | 960 |  | 18387 |  |  |  | InitiateAndContact # | 1919 | , # | 1920
2260 | 0x03 | R | 64 | Trip coil 1 전류 # | 961 | 16-bit unsigned integer | 4564 | 0x03 | R | 64 | Trip coil 2 전류 # | 961 | 16-bit unsigned integer | 6868 | 0x03 | R | 64 | Close coil 전류 # | 961 | 16-bit unsigned integer | 9172 | 0x03 | R | 64 | 전압 # | 961 | 16-bit signed integer | 11476 | 0x03 | R | 64 | A상 전류 # | 961 | 16-bit signed integer | 13780 | 0x03 | R | 64 | B상 전류 # | 961 | 16-bit signed integer | 16084 | 0x03 | R | 64 | C상 전류 # | 961 | 16-bit signed integer | 18388 | 0x03 | R | 64 | InitiateAndContact # | 1921 | , # | 1922 | 16-bit signed integer
2261 |  |  |  | Trip coil 1 전류 # | 962 |  | 4565 |  |  |  | Trip coil 2 전류 # | 962 |  | 6869 |  |  |  | Close coil 전류 # | 962 |  | 9173 |  |  |  | 전압 # | 962 |  | 11477 |  |  |  | A상 전류 # | 962 |  | 13781 |  |  |  | B상 전류 # | 962 |  | 16085 |  |  |  | C상 전류 # | 962 |  | 18389 |  |  |  | InitiateAndContact # | 1923 | , # | 1924
2262 |  |  |  | Trip coil 1 전류 # | 963 |  | 4566 |  |  |  | Trip coil 2 전류 # | 963 |  | 6870 |  |  |  | Close coil 전류 # | 963 |  | 9174 |  |  |  | 전압 # | 963 |  | 11478 |  |  |  | A상 전류 # | 963 |  | 13782 |  |  |  | B상 전류 # | 963 |  | 16086 |  |  |  | C상 전류 # | 963 |  | 18390 |  |  |  | InitiateAndContact # | 1925 | , # | 1926
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2321 |  |  |  | Trip coil 1 전류 # | 1022 |  | 4625 |  |  |  | Trip coil 2 전류 # | 1022 |  | 6929 |  |  |  | Close coil 전류 # | 1022 |  | 9233 |  |  |  | 전압 # | 1022 |  | 11537 |  |  |  | A상 전류 # | 1022 |  | 13841 |  |  |  | B상 전류 # | 1022 |  | 16145 |  |  |  | C상 전류 # | 1022 |  | 18449 |  |  |  | InitiateAndContact # | 2043 | , # | 2044
2322 |  |  |  | Trip coil 1 전류 # | 1023 |  | 4626 |  |  |  | Trip coil 2 전류 # | 1023 |  | 6930 |  |  |  | Close coil 전류 # | 1023 |  | 9234 |  |  |  | 전압 # | 1023 |  | 11538 |  |  |  | A상 전류 # | 1023 |  | 13842 |  |  |  | B상 전류 # | 1023 |  | 16146 |  |  |  | C상 전류 # | 1023 |  | 18450 |  |  |  | InitiateAndContact # | 2045 | , # | 2046
2323 |  |  |  | Trip coil 1 전류 # | 1024 |  | 4627 |  |  |  | Trip coil 2 전류 # | 1024 |  | 6931 |  |  |  | Close coil 전류 # | 1024 |  | 9235 |  |  |  | 전압 # | 1024 |  | 11539 |  |  |  | A상 전류 # | 1024 |  | 13843 |  |  |  | B상 전류 # | 1024 |  | 16147 |  |  |  | C상 전류 # | 1024 |  | 18451 |  |  |  | InitiateAndContact # | 2047 | , # | 2048
2324 | 0x03 | R | 64 | Trip coil 1 전류 # | 1025 | 16-bit unsigned integer | 4628 | 0x03 | R | 64 | Trip coil 2 전류 # | 1025 | 16-bit unsigned integer | 6932 | 0x03 | R | 64 | Close coil 전류 # | 1025 | 16-bit unsigned integer | 9236 | 0x03 | R | 64 | 전압 # | 1025 | 16-bit signed integer | 11540 | 0x03 | R | 64 | A상 전류 # | 1025 | 16-bit signed integer | 13844 | 0x03 | R | 64 | B상 전류 # | 1025 | 16-bit signed integer | 16148 | 0x03 | R | 64 | C상 전류 # | 1025 | 16-bit signed integer | 18452 | 0x03 | R | 64 | InitiateAndContact # | 2049 | , # | 2050 | 16-bit signed integer
2325 |  |  |  | Trip coil 1 전류 # | 1026 |  | 4629 |  |  |  | Trip coil 2 전류 # | 1026 |  | 6933 |  |  |  | Close coil 전류 # | 1026 |  | 9237 |  |  |  | 전압 # | 1026 |  | 11541 |  |  |  | A상 전류 # | 1026 |  | 13845 |  |  |  | B상 전류 # | 1026 |  | 16149 |  |  |  | C상 전류 # | 1026 |  | 18453 |  |  |  | InitiateAndContact # | 2051 | , # | 2052
2326 |  |  |  | Trip coil 1 전류 # | 1027 |  | 4630 |  |  |  | Trip coil 2 전류 # | 1027 |  | 6934 |  |  |  | Close coil 전류 # | 1027 |  | 9238 |  |  |  | 전압 # | 1027 |  | 11542 |  |  |  | A상 전류 # | 1027 |  | 13846 |  |  |  | B상 전류 # | 1027 |  | 16150 |  |  |  | C상 전류 # | 1027 |  | 18454 |  |  |  | InitiateAndContact # | 2053 | , # | 2054
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2385 |  |  |  | Trip coil 1 전류 # | 1086 |  | 4689 |  |  |  | Trip coil 2 전류 # | 1086 |  | 6993 |  |  |  | Close coil 전류 # | 1086 |  | 9297 |  |  |  | 전압 # | 1086 |  | 11601 |  |  |  | A상 전류 # | 1086 |  | 13905 |  |  |  | B상 전류 # | 1086 |  | 16209 |  |  |  | C상 전류 # | 1086 |  | 18513 |  |  |  | InitiateAndContact # | 2171 | , # | 2172
2386 |  |  |  | Trip coil 1 전류 # | 1087 |  | 4690 |  |  |  | Trip coil 2 전류 # | 1087 |  | 6994 |  |  |  | Close coil 전류 # | 1087 |  | 9298 |  |  |  | 전압 # | 1087 |  | 11602 |  |  |  | A상 전류 # | 1087 |  | 13906 |  |  |  | B상 전류 # | 1087 |  | 16210 |  |  |  | C상 전류 # | 1087 |  | 18514 |  |  |  | InitiateAndContact # | 2173 | , # | 2174
2387 |  |  |  | Trip coil 1 전류 # | 1088 |  | 4691 |  |  |  | Trip coil 2 전류 # | 1088 |  | 6995 |  |  |  | Close coil 전류 # | 1088 |  | 9299 |  |  |  | 전압 # | 1088 |  | 11603 |  |  |  | A상 전류 # | 1088 |  | 13907 |  |  |  | B상 전류 # | 1088 |  | 16211 |  |  |  | C상 전류 # | 1088 |  | 18515 |  |  |  | InitiateAndContact # | 2175 | , # | 2176
2388 | 0x03 | R | 64 | Trip coil 1 전류 # | 1089 | 16-bit unsigned integer | 4692 | 0x03 | R | 64 | Trip coil 2 전류 # | 1089 | 16-bit unsigned integer | 6996 | 0x03 | R | 64 | Close coil 전류 # | 1089 | 16-bit unsigned integer | 9300 | 0x03 | R | 64 | 전압 # | 1089 | 16-bit signed integer | 11604 | 0x03 | R | 64 | A상 전류 # | 1089 | 16-bit signed integer | 13908 | 0x03 | R | 64 | B상 전류 # | 1089 | 16-bit signed integer | 16212 | 0x03 | R | 64 | C상 전류 # | 1089 | 16-bit signed integer | 18516 | 0x03 | R | 64 | InitiateAndContact # | 2177 | , # | 2178 | 16-bit signed integer
2389 |  |  |  | Trip coil 1 전류 # | 1090 |  | 4693 |  |  |  | Trip coil 2 전류 # | 1090 |  | 6997 |  |  |  | Close coil 전류 # | 1090 |  | 9301 |  |  |  | 전압 # | 1090 |  | 11605 |  |  |  | A상 전류 # | 1090 |  | 13909 |  |  |  | B상 전류 # | 1090 |  | 16213 |  |  |  | C상 전류 # | 1090 |  | 18517 |  |  |  | InitiateAndContact # | 2179 | , # | 2180
2390 |  |  |  | Trip coil 1 전류 # | 1091 |  | 4694 |  |  |  | Trip coil 2 전류 # | 1091 |  | 6998 |  |  |  | Close coil 전류 # | 1091 |  | 9302 |  |  |  | 전압 # | 1091 |  | 11606 |  |  |  | A상 전류 # | 1091 |  | 13910 |  |  |  | B상 전류 # | 1091 |  | 16214 |  |  |  | C상 전류 # | 1091 |  | 18518 |  |  |  | InitiateAndContact # | 2181 | , # | 2182
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2449 |  |  |  | Trip coil 1 전류 # | 1150 |  | 4753 |  |  |  | Trip coil 2 전류 # | 1150 |  | 7057 |  |  |  | Close coil 전류 # | 1150 |  | 9361 |  |  |  | 전압 # | 1150 |  | 11665 |  |  |  | A상 전류 # | 1150 |  | 13969 |  |  |  | B상 전류 # | 1150 |  | 16273 |  |  |  | C상 전류 # | 1150 |  | 18577 |  |  |  | InitiateAndContact # | 2299 | , # | 2300
2450 |  |  |  | Trip coil 1 전류 # | 1151 |  | 4754 |  |  |  | Trip coil 2 전류 # | 1151 |  | 7058 |  |  |  | Close coil 전류 # | 1151 |  | 9362 |  |  |  | 전압 # | 1151 |  | 11666 |  |  |  | A상 전류 # | 1151 |  | 13970 |  |  |  | B상 전류 # | 1151 |  | 16274 |  |  |  | C상 전류 # | 1151 |  | 18578 |  |  |  | InitiateAndContact # | 2301 | , # | 2302
2451 |  |  |  | Trip coil 1 전류 # | 1152 |  | 4755 |  |  |  | Trip coil 2 전류 # | 1152 |  | 7059 |  |  |  | Close coil 전류 # | 1152 |  | 9363 |  |  |  | 전압 # | 1152 |  | 11667 |  |  |  | A상 전류 # | 1152 |  | 13971 |  |  |  | B상 전류 # | 1152 |  | 16275 |  |  |  | C상 전류 # | 1152 |  | 18579 |  |  |  | InitiateAndContact # | 2303 | , # | 2304
2452 | 0x03 | R | 64 | Trip coil 1 전류 # | 1153 | 16-bit unsigned integer | 4756 | 0x03 | R | 64 | Trip coil 2 전류 # | 1153 | 16-bit unsigned integer | 7060 | 0x03 | R | 64 | Close coil 전류 # | 1153 | 16-bit unsigned integer | 9364 | 0x03 | R | 64 | 전압 # | 1153 | 16-bit signed integer | 11668 | 0x03 | R | 64 | A상 전류 # | 1153 | 16-bit signed integer | 13972 | 0x03 | R | 64 | B상 전류 # | 1153 | 16-bit signed integer | 16276 | 0x03 | R | 64 | C상 전류 # | 1153 | 16-bit signed integer
2453 |  |  |  | Trip coil 1 전류 # | 1154 |  | 4757 |  |  |  | Trip coil 2 전류 # | 1154 |  | 7061 |  |  |  | Close coil 전류 # | 1154 |  | 9365 |  |  |  | 전압 # | 1154 |  | 11669 |  |  |  | A상 전류 # | 1154 |  | 13973 |  |  |  | B상 전류 # | 1154 |  | 16277 |  |  |  | C상 전류 # | 1154
2454 |  |  |  | Trip coil 1 전류 # | 1155 |  | 4758 |  |  |  | Trip coil 2 전류 # | 1155 |  | 7062 |  |  |  | Close coil 전류 # | 1155 |  | 9366 |  |  |  | 전압 # | 1155 |  | 11670 |  |  |  | A상 전류 # | 1155 |  | 13974 |  |  |  | B상 전류 # | 1155 |  | 16278 |  |  |  | C상 전류 # | 1155
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2513 |  |  |  | Trip coil 1 전류 # | 1214 |  | 4817 |  |  |  | Trip coil 2 전류 # | 1214 |  | 7121 |  |  |  | Close coil 전류 # | 1214 |  | 9425 |  |  |  | 전압 # | 1214 |  | 11729 |  |  |  | A상 전류 # | 1214 |  | 14033 |  |  |  | B상 전류 # | 1214 |  | 16337 |  |  |  | C상 전류 # | 1214
2514 |  |  |  | Trip coil 1 전류 # | 1215 |  | 4818 |  |  |  | Trip coil 2 전류 # | 1215 |  | 7122 |  |  |  | Close coil 전류 # | 1215 |  | 9426 |  |  |  | 전압 # | 1215 |  | 11730 |  |  |  | A상 전류 # | 1215 |  | 14034 |  |  |  | B상 전류 # | 1215 |  | 16338 |  |  |  | C상 전류 # | 1215
2515 |  |  |  | Trip coil 1 전류 # | 1216 |  | 4819 |  |  |  | Trip coil 2 전류 # | 1216 |  | 7123 |  |  |  | Close coil 전류 # | 1216 |  | 9427 |  |  |  | 전압 # | 1216 |  | 11731 |  |  |  | A상 전류 # | 1216 |  | 14035 |  |  |  | B상 전류 # | 1216 |  | 16339 |  |  |  | C상 전류 # | 1216
2516 | 0x03 | R | 64 | Trip coil 1 전류 # | 1217 | 16-bit unsigned integer | 4820 | 0x03 | R | 64 | Trip coil 2 전류 # | 1217 | 16-bit unsigned integer | 7124 | 0x03 | R | 64 | Close coil 전류 # | 1217 | 16-bit unsigned integer | 9428 | 0x03 | R | 64 | 전압 # | 1217 | 16-bit signed integer | 11732 | 0x03 | R | 64 | A상 전류 # | 1217 | 16-bit signed integer | 14036 | 0x03 | R | 64 | B상 전류 # | 1217 | 16-bit signed integer | 16340 | 0x03 | R | 64 | C상 전류 # | 1217 | 16-bit signed integer
2517 |  |  |  | Trip coil 1 전류 # | 1218 |  | 4821 |  |  |  | Trip coil 2 전류 # | 1218 |  | 7125 |  |  |  | Close coil 전류 # | 1218 |  | 9429 |  |  |  | 전압 # | 1218 |  | 11733 |  |  |  | A상 전류 # | 1218 |  | 14037 |  |  |  | B상 전류 # | 1218 |  | 16341 |  |  |  | C상 전류 # | 1218
2518 |  |  |  | Trip coil 1 전류 # | 1219 |  | 4822 |  |  |  | Trip coil 2 전류 # | 1219 |  | 7126 |  |  |  | Close coil 전류 # | 1219 |  | 9430 |  |  |  | 전압 # | 1219 |  | 11734 |  |  |  | A상 전류 # | 1219 |  | 14038 |  |  |  | B상 전류 # | 1219 |  | 16342 |  |  |  | C상 전류 # | 1219
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2577 |  |  |  | Trip coil 1 전류 # | 1278 |  | 4881 |  |  |  | Trip coil 2 전류 # | 1278 |  | 7185 |  |  |  | Close coil 전류 # | 1278 |  | 9489 |  |  |  | 전압 # | 1278 |  | 11793 |  |  |  | A상 전류 # | 1278 |  | 14097 |  |  |  | B상 전류 # | 1278 |  | 16401 |  |  |  | C상 전류 # | 1278
2578 |  |  |  | Trip coil 1 전류 # | 1279 |  | 4882 |  |  |  | Trip coil 2 전류 # | 1279 |  | 7186 |  |  |  | Close coil 전류 # | 1279 |  | 9490 |  |  |  | 전압 # | 1279 |  | 11794 |  |  |  | A상 전류 # | 1279 |  | 14098 |  |  |  | B상 전류 # | 1279 |  | 16402 |  |  |  | C상 전류 # | 1279
2579 |  |  |  | Trip coil 1 전류 # | 1280 |  | 4883 |  |  |  | Trip coil 2 전류 # | 1280 |  | 7187 |  |  |  | Close coil 전류 # | 1280 |  | 9491 |  |  |  | 전압 # | 1280 |  | 11795 |  |  |  | A상 전류 # | 1280 |  | 14099 |  |  |  | B상 전류 # | 1280 |  | 16403 |  |  |  | C상 전류 # | 1280
2580 | 0x03 | R | 64 | Trip coil 1 전류 # | 1281 | 16-bit unsigned integer | 4884 | 0x03 | R | 64 | Trip coil 2 전류 # | 1281 | 16-bit unsigned integer | 7188 | 0x03 | R | 64 | Close coil 전류 # | 1281 | 16-bit unsigned integer | 9492 | 0x03 | R | 64 | 전압 # | 1281 | 16-bit signed integer | 11796 | 0x03 | R | 64 | A상 전류 # | 1281 | 16-bit signed integer | 14100 | 0x03 | R | 64 | B상 전류 # | 1281 | 16-bit signed integer | 16404 | 0x03 | R | 64 | C상 전류 # | 1281 | 16-bit signed integer
2581 |  |  |  | Trip coil 1 전류 # | 1282 |  | 4885 |  |  |  | Trip coil 2 전류 # | 1282 |  | 7189 |  |  |  | Close coil 전류 # | 1282 |  | 9493 |  |  |  | 전압 # | 1282 |  | 11797 |  |  |  | A상 전류 # | 1282 |  | 14101 |  |  |  | B상 전류 # | 1282 |  | 16405 |  |  |  | C상 전류 # | 1282
2582 |  |  |  | Trip coil 1 전류 # | 1283 |  | 4886 |  |  |  | Trip coil 2 전류 # | 1283 |  | 7190 |  |  |  | Close coil 전류 # | 1283 |  | 9494 |  |  |  | 전압 # | 1283 |  | 11798 |  |  |  | A상 전류 # | 1283 |  | 14102 |  |  |  | B상 전류 # | 1283 |  | 16406 |  |  |  | C상 전류 # | 1283
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2641 |  |  |  | Trip coil 1 전류 # | 1342 |  | 4945 |  |  |  | Trip coil 2 전류 # | 1342 |  | 7249 |  |  |  | Close coil 전류 # | 1342 |  | 9553 |  |  |  | 전압 # | 1342 |  | 11857 |  |  |  | A상 전류 # | 1342 |  | 14161 |  |  |  | B상 전류 # | 1342 |  | 16465 |  |  |  | C상 전류 # | 1342
2642 |  |  |  | Trip coil 1 전류 # | 1343 |  | 4946 |  |  |  | Trip coil 2 전류 # | 1343 |  | 7250 |  |  |  | Close coil 전류 # | 1343 |  | 9554 |  |  |  | 전압 # | 1343 |  | 11858 |  |  |  | A상 전류 # | 1343 |  | 14162 |  |  |  | B상 전류 # | 1343 |  | 16466 |  |  |  | C상 전류 # | 1343
2643 |  |  |  | Trip coil 1 전류 # | 1344 |  | 4947 |  |  |  | Trip coil 2 전류 # | 1344 |  | 7251 |  |  |  | Close coil 전류 # | 1344 |  | 9555 |  |  |  | 전압 # | 1344 |  | 11859 |  |  |  | A상 전류 # | 1344 |  | 14163 |  |  |  | B상 전류 # | 1344 |  | 16467 |  |  |  | C상 전류 # | 1344
2644 | 0x03 | R | 64 | Trip coil 1 전류 # | 1345 | 16-bit unsigned integer | 4948 | 0x03 | R | 64 | Trip coil 2 전류 # | 1345 | 16-bit unsigned integer | 7252 | 0x03 | R | 64 | Close coil 전류 # | 1345 | 16-bit unsigned integer | 9556 | 0x03 | R | 64 | 전압 # | 1345 | 16-bit signed integer | 11860 | 0x03 | R | 64 | A상 전류 # | 1345 | 16-bit signed integer | 14164 | 0x03 | R | 64 | B상 전류 # | 1345 | 16-bit signed integer | 16468 | 0x03 | R | 64 | C상 전류 # | 1345 | 16-bit signed integer
2645 |  |  |  | Trip coil 1 전류 # | 1346 |  | 4949 |  |  |  | Trip coil 2 전류 # | 1346 |  | 7253 |  |  |  | Close coil 전류 # | 1346 |  | 9557 |  |  |  | 전압 # | 1346 |  | 11861 |  |  |  | A상 전류 # | 1346 |  | 14165 |  |  |  | B상 전류 # | 1346 |  | 16469 |  |  |  | C상 전류 # | 1346
2646 |  |  |  | Trip coil 1 전류 # | 1347 |  | 4950 |  |  |  | Trip coil 2 전류 # | 1347 |  | 7254 |  |  |  | Close coil 전류 # | 1347 |  | 9558 |  |  |  | 전압 # | 1347 |  | 11862 |  |  |  | A상 전류 # | 1347 |  | 14166 |  |  |  | B상 전류 # | 1347 |  | 16470 |  |  |  | C상 전류 # | 1347
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2705 |  |  |  | Trip coil 1 전류 # | 1406 |  | 5009 |  |  |  | Trip coil 2 전류 # | 1406 |  | 7313 |  |  |  | Close coil 전류 # | 1406 |  | 9617 |  |  |  | 전압 # | 1406 |  | 11921 |  |  |  | A상 전류 # | 1406 |  | 14225 |  |  |  | B상 전류 # | 1406 |  | 16529 |  |  |  | C상 전류 # | 1406
2706 |  |  |  | Trip coil 1 전류 # | 1407 |  | 5010 |  |  |  | Trip coil 2 전류 # | 1407 |  | 7314 |  |  |  | Close coil 전류 # | 1407 |  | 9618 |  |  |  | 전압 # | 1407 |  | 11922 |  |  |  | A상 전류 # | 1407 |  | 14226 |  |  |  | B상 전류 # | 1407 |  | 16530 |  |  |  | C상 전류 # | 1407
2707 |  |  |  | Trip coil 1 전류 # | 1408 |  | 5011 |  |  |  | Trip coil 2 전류 # | 1408 |  | 7315 |  |  |  | Close coil 전류 # | 1408 |  | 9619 |  |  |  | 전압 # | 1408 |  | 11923 |  |  |  | A상 전류 # | 1408 |  | 14227 |  |  |  | B상 전류 # | 1408 |  | 16531 |  |  |  | C상 전류 # | 1408
2708 | 0x03 | R | 64 | Trip coil 1 전류 # | 1409 | 16-bit unsigned integer | 5012 | 0x03 | R | 64 | Trip coil 2 전류 # | 1409 | 16-bit unsigned integer | 7316 | 0x03 | R | 64 | Close coil 전류 # | 1409 | 16-bit unsigned integer | 9620 | 0x03 | R | 64 | 전압 # | 1409 | 16-bit signed integer | 11924 | 0x03 | R | 64 | A상 전류 # | 1409 | 16-bit signed integer | 14228 | 0x03 | R | 64 | B상 전류 # | 1409 | 16-bit signed integer | 16532 | 0x03 | R | 64 | C상 전류 # | 1409 | 16-bit signed integer
2709 |  |  |  | Trip coil 1 전류 # | 1410 |  | 5013 |  |  |  | Trip coil 2 전류 # | 1410 |  | 7317 |  |  |  | Close coil 전류 # | 1410 |  | 9621 |  |  |  | 전압 # | 1410 |  | 11925 |  |  |  | A상 전류 # | 1410 |  | 14229 |  |  |  | B상 전류 # | 1410 |  | 16533 |  |  |  | C상 전류 # | 1410
2710 |  |  |  | Trip coil 1 전류 # | 1411 |  | 5014 |  |  |  | Trip coil 2 전류 # | 1411 |  | 7318 |  |  |  | Close coil 전류 # | 1411 |  | 9622 |  |  |  | 전압 # | 1411 |  | 11926 |  |  |  | A상 전류 # | 1411 |  | 14230 |  |  |  | B상 전류 # | 1411 |  | 16534 |  |  |  | C상 전류 # | 1411
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2769 |  |  |  | Trip coil 1 전류 # | 1470 |  | 5073 |  |  |  | Trip coil 2 전류 # | 1470 |  | 7377 |  |  |  | Close coil 전류 # | 1470 |  | 9681 |  |  |  | 전압 # | 1470 |  | 11985 |  |  |  | A상 전류 # | 1470 |  | 14289 |  |  |  | B상 전류 # | 1470 |  | 16593 |  |  |  | C상 전류 # | 1470
2770 |  |  |  | Trip coil 1 전류 # | 1471 |  | 5074 |  |  |  | Trip coil 2 전류 # | 1471 |  | 7378 |  |  |  | Close coil 전류 # | 1471 |  | 9682 |  |  |  | 전압 # | 1471 |  | 11986 |  |  |  | A상 전류 # | 1471 |  | 14290 |  |  |  | B상 전류 # | 1471 |  | 16594 |  |  |  | C상 전류 # | 1471
2771 |  |  |  | Trip coil 1 전류 # | 1472 |  | 5075 |  |  |  | Trip coil 2 전류 # | 1472 |  | 7379 |  |  |  | Close coil 전류 # | 1472 |  | 9683 |  |  |  | 전압 # | 1472 |  | 11987 |  |  |  | A상 전류 # | 1472 |  | 14291 |  |  |  | B상 전류 # | 1472 |  | 16595 |  |  |  | C상 전류 # | 1472
2772 | 0x03 | R | 64 | Trip coil 1 전류 # | 1473 | 16-bit unsigned integer | 5076 | 0x03 | R | 64 | Trip coil 2 전류 # | 1473 | 16-bit unsigned integer | 7380 | 0x03 | R | 64 | Close coil 전류 # | 1473 | 16-bit unsigned integer | 9684 | 0x03 | R | 64 | 전압 # | 1473 | 16-bit signed integer | 11988 | 0x03 | R | 64 | A상 전류 # | 1473 | 16-bit signed integer | 14292 | 0x03 | R | 64 | B상 전류 # | 1473 | 16-bit signed integer | 16596 | 0x03 | R | 64 | C상 전류 # | 1473 | 16-bit signed integer
2773 |  |  |  | Trip coil 1 전류 # | 1474 |  | 5077 |  |  |  | Trip coil 2 전류 # | 1474 |  | 7381 |  |  |  | Close coil 전류 # | 1474 |  | 9685 |  |  |  | 전압 # | 1474 |  | 11989 |  |  |  | A상 전류 # | 1474 |  | 14293 |  |  |  | B상 전류 # | 1474 |  | 16597 |  |  |  | C상 전류 # | 1474
2774 |  |  |  | Trip coil 1 전류 # | 1475 |  | 5078 |  |  |  | Trip coil 2 전류 # | 1475 |  | 7382 |  |  |  | Close coil 전류 # | 1475 |  | 9686 |  |  |  | 전압 # | 1475 |  | 11990 |  |  |  | A상 전류 # | 1475 |  | 14294 |  |  |  | B상 전류 # | 1475 |  | 16598 |  |  |  | C상 전류 # | 1475
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2833 |  |  |  | Trip coil 1 전류 # | 1534 |  | 5137 |  |  |  | Trip coil 2 전류 # | 1534 |  | 7441 |  |  |  | Close coil 전류 # | 1534 |  | 9745 |  |  |  | 전압 # | 1534 |  | 12049 |  |  |  | A상 전류 # | 1534 |  | 14353 |  |  |  | B상 전류 # | 1534 |  | 16657 |  |  |  | C상 전류 # | 1534
2834 |  |  |  | Trip coil 1 전류 # | 1535 |  | 5138 |  |  |  | Trip coil 2 전류 # | 1535 |  | 7442 |  |  |  | Close coil 전류 # | 1535 |  | 9746 |  |  |  | 전압 # | 1535 |  | 12050 |  |  |  | A상 전류 # | 1535 |  | 14354 |  |  |  | B상 전류 # | 1535 |  | 16658 |  |  |  | C상 전류 # | 1535
2835 |  |  |  | Trip coil 1 전류 # | 1536 |  | 5139 |  |  |  | Trip coil 2 전류 # | 1536 |  | 7443 |  |  |  | Close coil 전류 # | 1536 |  | 9747 |  |  |  | 전압 # | 1536 |  | 12051 |  |  |  | A상 전류 # | 1536 |  | 14355 |  |  |  | B상 전류 # | 1536 |  | 16659 |  |  |  | C상 전류 # | 1536
2836 | 0x03 | R | 64 | Trip coil 1 전류 # | 1537 | 16-bit unsigned integer | 5140 | 0x03 | R | 64 | Trip coil 2 전류 # | 1537 | 16-bit unsigned integer | 7444 | 0x03 | R | 64 | Close coil 전류 # | 1537 | 16-bit unsigned integer | 9748 | 0x03 | R | 64 | 전압 # | 1537 | 16-bit signed integer | 12052 | 0x03 | R | 64 | A상 전류 # | 1537 | 16-bit signed integer | 14356 | 0x03 | R | 64 | B상 전류 # | 1537 | 16-bit signed integer | 16660 | 0x03 | R | 64 | C상 전류 # | 1537 | 16-bit signed integer
2837 |  |  |  | Trip coil 1 전류 # | 1538 |  | 5141 |  |  |  | Trip coil 2 전류 # | 1538 |  | 7445 |  |  |  | Close coil 전류 # | 1538 |  | 9749 |  |  |  | 전압 # | 1538 |  | 12053 |  |  |  | A상 전류 # | 1538 |  | 14357 |  |  |  | B상 전류 # | 1538 |  | 16661 |  |  |  | C상 전류 # | 1538
2838 |  |  |  | Trip coil 1 전류 # | 1539 |  | 5142 |  |  |  | Trip coil 2 전류 # | 1539 |  | 7446 |  |  |  | Close coil 전류 # | 1539 |  | 9750 |  |  |  | 전압 # | 1539 |  | 12054 |  |  |  | A상 전류 # | 1539 |  | 14358 |  |  |  | B상 전류 # | 1539 |  | 16662 |  |  |  | C상 전류 # | 1539
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2897 |  |  |  | Trip coil 1 전류 # | 1598 |  | 5201 |  |  |  | Trip coil 2 전류 # | 1598 |  | 7505 |  |  |  | Close coil 전류 # | 1598 |  | 9809 |  |  |  | 전압 # | 1598 |  | 12113 |  |  |  | A상 전류 # | 1598 |  | 14417 |  |  |  | B상 전류 # | 1598 |  | 16721 |  |  |  | C상 전류 # | 1598
2898 |  |  |  | Trip coil 1 전류 # | 1599 |  | 5202 |  |  |  | Trip coil 2 전류 # | 1599 |  | 7506 |  |  |  | Close coil 전류 # | 1599 |  | 9810 |  |  |  | 전압 # | 1599 |  | 12114 |  |  |  | A상 전류 # | 1599 |  | 14418 |  |  |  | B상 전류 # | 1599 |  | 16722 |  |  |  | C상 전류 # | 1599
2899 |  |  |  | Trip coil 1 전류 # | 1600 |  | 5203 |  |  |  | Trip coil 2 전류 # | 1600 |  | 7507 |  |  |  | Close coil 전류 # | 1600 |  | 9811 |  |  |  | 전압 # | 1600 |  | 12115 |  |  |  | A상 전류 # | 1600 |  | 14419 |  |  |  | B상 전류 # | 1600 |  | 16723 |  |  |  | C상 전류 # | 1600
2900 | 0x03 | R | 64 | Trip coil 1 전류 # | 1601 | 16-bit unsigned integer | 5204 | 0x03 | R | 64 | Trip coil 2 전류 # | 1601 | 16-bit unsigned integer | 7508 | 0x03 | R | 64 | Close coil 전류 # | 1601 | 16-bit unsigned integer | 9812 | 0x03 | R | 64 | 전압 # | 1601 | 16-bit signed integer | 12116 | 0x03 | R | 64 | A상 전류 # | 1601 | 16-bit signed integer | 14420 | 0x03 | R | 64 | B상 전류 # | 1601 | 16-bit signed integer | 16724 | 0x03 | R | 64 | C상 전류 # | 1601 | 16-bit signed integer
2901 |  |  |  | Trip coil 1 전류 # | 1602 |  | 5205 |  |  |  | Trip coil 2 전류 # | 1602 |  | 7509 |  |  |  | Close coil 전류 # | 1602 |  | 9813 |  |  |  | 전압 # | 1602 |  | 12117 |  |  |  | A상 전류 # | 1602 |  | 14421 |  |  |  | B상 전류 # | 1602 |  | 16725 |  |  |  | C상 전류 # | 1602
2902 |  |  |  | Trip coil 1 전류 # | 1603 |  | 5206 |  |  |  | Trip coil 2 전류 # | 1603 |  | 7510 |  |  |  | Close coil 전류 # | 1603 |  | 9814 |  |  |  | 전압 # | 1603 |  | 12118 |  |  |  | A상 전류 # | 1603 |  | 14422 |  |  |  | B상 전류 # | 1603 |  | 16726 |  |  |  | C상 전류 # | 1603
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
2961 |  |  |  | Trip coil 1 전류 # | 1662 |  | 5265 |  |  |  | Trip coil 2 전류 # | 1662 |  | 7569 |  |  |  | Close coil 전류 # | 1662 |  | 9873 |  |  |  | 전압 # | 1662 |  | 12177 |  |  |  | A상 전류 # | 1662 |  | 14481 |  |  |  | B상 전류 # | 1662 |  | 16785 |  |  |  | C상 전류 # | 1662
2962 |  |  |  | Trip coil 1 전류 # | 1663 |  | 5266 |  |  |  | Trip coil 2 전류 # | 1663 |  | 7570 |  |  |  | Close coil 전류 # | 1663 |  | 9874 |  |  |  | 전압 # | 1663 |  | 12178 |  |  |  | A상 전류 # | 1663 |  | 14482 |  |  |  | B상 전류 # | 1663 |  | 16786 |  |  |  | C상 전류 # | 1663
2963 |  |  |  | Trip coil 1 전류 # | 1664 |  | 5267 |  |  |  | Trip coil 2 전류 # | 1664 |  | 7571 |  |  |  | Close coil 전류 # | 1664 |  | 9875 |  |  |  | 전압 # | 1664 |  | 12179 |  |  |  | A상 전류 # | 1664 |  | 14483 |  |  |  | B상 전류 # | 1664 |  | 16787 |  |  |  | C상 전류 # | 1664
2964 | 0x03 | R | 64 | Trip coil 1 전류 # | 1665 | 16-bit unsigned integer | 5268 | 0x03 | R | 64 | Trip coil 2 전류 # | 1665 | 16-bit unsigned integer | 7572 | 0x03 | R | 64 | Close coil 전류 # | 1665 | 16-bit unsigned integer | 9876 | 0x03 | R | 64 | 전압 # | 1665 | 16-bit signed integer | 12180 | 0x03 | R | 64 | A상 전류 # | 1665 | 16-bit signed integer | 14484 | 0x03 | R | 64 | B상 전류 # | 1665 | 16-bit signed integer | 16788 | 0x03 | R | 64 | C상 전류 # | 1665 | 16-bit signed integer
2965 |  |  |  | Trip coil 1 전류 # | 1666 |  | 5269 |  |  |  | Trip coil 2 전류 # | 1666 |  | 7573 |  |  |  | Close coil 전류 # | 1666 |  | 9877 |  |  |  | 전압 # | 1666 |  | 12181 |  |  |  | A상 전류 # | 1666 |  | 14485 |  |  |  | B상 전류 # | 1666 |  | 16789 |  |  |  | C상 전류 # | 1666
2966 |  |  |  | Trip coil 1 전류 # | 1667 |  | 5270 |  |  |  | Trip coil 2 전류 # | 1667 |  | 7574 |  |  |  | Close coil 전류 # | 1667 |  | 9878 |  |  |  | 전압 # | 1667 |  | 12182 |  |  |  | A상 전류 # | 1667 |  | 14486 |  |  |  | B상 전류 # | 1667 |  | 16790 |  |  |  | C상 전류 # | 1667
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
3025 |  |  |  | Trip coil 1 전류 # | 1726 |  | 5329 |  |  |  | Trip coil 2 전류 # | 1726 |  | 7633 |  |  |  | Close coil 전류 # | 1726 |  | 9937 |  |  |  | 전압 # | 1726 |  | 12241 |  |  |  | A상 전류 # | 1726 |  | 14545 |  |  |  | B상 전류 # | 1726 |  | 16849 |  |  |  | C상 전류 # | 1726
3026 |  |  |  | Trip coil 1 전류 # | 1727 |  | 5330 |  |  |  | Trip coil 2 전류 # | 1727 |  | 7634 |  |  |  | Close coil 전류 # | 1727 |  | 9938 |  |  |  | 전압 # | 1727 |  | 12242 |  |  |  | A상 전류 # | 1727 |  | 14546 |  |  |  | B상 전류 # | 1727 |  | 16850 |  |  |  | C상 전류 # | 1727
3027 |  |  |  | Trip coil 1 전류 # | 1728 |  | 5331 |  |  |  | Trip coil 2 전류 # | 1728 |  | 7635 |  |  |  | Close coil 전류 # | 1728 |  | 9939 |  |  |  | 전압 # | 1728 |  | 12243 |  |  |  | A상 전류 # | 1728 |  | 14547 |  |  |  | B상 전류 # | 1728 |  | 16851 |  |  |  | C상 전류 # | 1728
3028 | 0x03 | R | 64 | Trip coil 1 전류 # | 1729 | 16-bit unsigned integer | 5332 | 0x03 | R | 64 | Trip coil 2 전류 # | 1729 | 16-bit unsigned integer | 7636 | 0x03 | R | 64 | Close coil 전류 # | 1729 | 16-bit unsigned integer | 9940 | 0x03 | R | 64 | 전압 # | 1729 | 16-bit signed integer | 12244 | 0x03 | R | 64 | A상 전류 # | 1729 | 16-bit signed integer | 14548 | 0x03 | R | 64 | B상 전류 # | 1729 | 16-bit signed integer | 16852 | 0x03 | R | 64 | C상 전류 # | 1729 | 16-bit signed integer
3029 |  |  |  | Trip coil 1 전류 # | 1730 |  | 5333 |  |  |  | Trip coil 2 전류 # | 1730 |  | 7637 |  |  |  | Close coil 전류 # | 1730 |  | 9941 |  |  |  | 전압 # | 1730 |  | 12245 |  |  |  | A상 전류 # | 1730 |  | 14549 |  |  |  | B상 전류 # | 1730 |  | 16853 |  |  |  | C상 전류 # | 1730
3030 |  |  |  | Trip coil 1 전류 # | 1731 |  | 5334 |  |  |  | Trip coil 2 전류 # | 1731 |  | 7638 |  |  |  | Close coil 전류 # | 1731 |  | 9942 |  |  |  | 전압 # | 1731 |  | 12246 |  |  |  | A상 전류 # | 1731 |  | 14550 |  |  |  | B상 전류 # | 1731 |  | 16854 |  |  |  | C상 전류 # | 1731
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
3089 |  |  |  | Trip coil 1 전류 # | 1790 |  | 5393 |  |  |  | Trip coil 2 전류 # | 1790 |  | 7697 |  |  |  | Close coil 전류 # | 1790 |  | 10001 |  |  |  | 전압 # | 1790 |  | 12305 |  |  |  | A상 전류 # | 1790 |  | 14609 |  |  |  | B상 전류 # | 1790 |  | 16913 |  |  |  | C상 전류 # | 1790
3090 |  |  |  | Trip coil 1 전류 # | 1791 |  | 5394 |  |  |  | Trip coil 2 전류 # | 1791 |  | 7698 |  |  |  | Close coil 전류 # | 1791 |  | 10002 |  |  |  | 전압 # | 1791 |  | 12306 |  |  |  | A상 전류 # | 1791 |  | 14610 |  |  |  | B상 전류 # | 1791 |  | 16914 |  |  |  | C상 전류 # | 1791
3091 |  |  |  | Trip coil 1 전류 # | 1792 |  | 5395 |  |  |  | Trip coil 2 전류 # | 1792 |  | 7699 |  |  |  | Close coil 전류 # | 1792 |  | 10003 |  |  |  | 전압 # | 1792 |  | 12307 |  |  |  | A상 전류 # | 1792 |  | 14611 |  |  |  | B상 전류 # | 1792 |  | 16915 |  |  |  | C상 전류 # | 1792
3092 | 0x03 | R | 64 | Trip coil 1 전류 # | 1793 | 16-bit unsigned integer | 5396 | 0x03 | R | 64 | Trip coil 2 전류 # | 1793 | 16-bit unsigned integer | 7700 | 0x03 | R | 64 | Close coil 전류 # | 1793 | 16-bit unsigned integer | 10004 | 0x03 | R | 64 | 전압 # | 1793 | 16-bit signed integer | 12308 | 0x03 | R | 64 | A상 전류 # | 1793 | 16-bit signed integer | 14612 | 0x03 | R | 64 | B상 전류 # | 1793 | 16-bit signed integer | 16916 | 0x03 | R | 64 | C상 전류 # | 1793 | 16-bit signed integer
3093 |  |  |  | Trip coil 1 전류 # | 1794 |  | 5397 |  |  |  | Trip coil 2 전류 # | 1794 |  | 7701 |  |  |  | Close coil 전류 # | 1794 |  | 10005 |  |  |  | 전압 # | 1794 |  | 12309 |  |  |  | A상 전류 # | 1794 |  | 14613 |  |  |  | B상 전류 # | 1794 |  | 16917 |  |  |  | C상 전류 # | 1794
3094 |  |  |  | Trip coil 1 전류 # | 1795 |  | 5398 |  |  |  | Trip coil 2 전류 # | 1795 |  | 7702 |  |  |  | Close coil 전류 # | 1795 |  | 10006 |  |  |  | 전압 # | 1795 |  | 12310 |  |  |  | A상 전류 # | 1795 |  | 14614 |  |  |  | B상 전류 # | 1795 |  | 16918 |  |  |  | C상 전류 # | 1795
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
3153 |  |  |  | Trip coil 1 전류 # | 1854 |  | 5457 |  |  |  | Trip coil 2 전류 # | 1854 |  | 7761 |  |  |  | Close coil 전류 # | 1854 |  | 10065 |  |  |  | 전압 # | 1854 |  | 12369 |  |  |  | A상 전류 # | 1854 |  | 14673 |  |  |  | B상 전류 # | 1854 |  | 16977 |  |  |  | C상 전류 # | 1854
3154 |  |  |  | Trip coil 1 전류 # | 1855 |  | 5458 |  |  |  | Trip coil 2 전류 # | 1855 |  | 7762 |  |  |  | Close coil 전류 # | 1855 |  | 10066 |  |  |  | 전압 # | 1855 |  | 12370 |  |  |  | A상 전류 # | 1855 |  | 14674 |  |  |  | B상 전류 # | 1855 |  | 16978 |  |  |  | C상 전류 # | 1855
3155 |  |  |  | Trip coil 1 전류 # | 1856 |  | 5459 |  |  |  | Trip coil 2 전류 # | 1856 |  | 7763 |  |  |  | Close coil 전류 # | 1856 |  | 10067 |  |  |  | 전압 # | 1856 |  | 12371 |  |  |  | A상 전류 # | 1856 |  | 14675 |  |  |  | B상 전류 # | 1856 |  | 16979 |  |  |  | C상 전류 # | 1856
3156 | 0x03 | R | 64 | Trip coil 1 전류 # | 1857 | 16-bit unsigned integer | 5460 | 0x03 | R | 64 | Trip coil 2 전류 # | 1857 | 16-bit unsigned integer | 7764 | 0x03 | R | 64 | Close coil 전류 # | 1857 | 16-bit unsigned integer | 10068 | 0x03 | R | 64 | 전압 # | 1857 | 16-bit signed integer | 12372 | 0x03 | R | 64 | A상 전류 # | 1857 | 16-bit signed integer | 14676 | 0x03 | R | 64 | B상 전류 # | 1857 | 16-bit signed integer | 16980 | 0x03 | R | 64 | C상 전류 # | 1857 | 16-bit signed integer
3157 |  |  |  | Trip coil 1 전류 # | 1858 |  | 5461 |  |  |  | Trip coil 2 전류 # | 1858 |  | 7765 |  |  |  | Close coil 전류 # | 1858 |  | 10069 |  |  |  | 전압 # | 1858 |  | 12373 |  |  |  | A상 전류 # | 1858 |  | 14677 |  |  |  | B상 전류 # | 1858 |  | 16981 |  |  |  | C상 전류 # | 1858
3158 |  |  |  | Trip coil 1 전류 # | 1859 |  | 5462 |  |  |  | Trip coil 2 전류 # | 1859 |  | 7766 |  |  |  | Close coil 전류 # | 1859 |  | 10070 |  |  |  | 전압 # | 1859 |  | 12374 |  |  |  | A상 전류 # | 1859 |  | 14678 |  |  |  | B상 전류 # | 1859 |  | 16982 |  |  |  | C상 전류 # | 1859
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
3217 |  |  |  | Trip coil 1 전류 # | 1918 |  | 5521 |  |  |  | Trip coil 2 전류 # | 1918 |  | 7825 |  |  |  | Close coil 전류 # | 1918 |  | 10129 |  |  |  | 전압 # | 1918 |  | 12433 |  |  |  | A상 전류 # | 1918 |  | 14737 |  |  |  | B상 전류 # | 1918 |  | 17041 |  |  |  | C상 전류 # | 1918
3218 |  |  |  | Trip coil 1 전류 # | 1919 |  | 5522 |  |  |  | Trip coil 2 전류 # | 1919 |  | 7826 |  |  |  | Close coil 전류 # | 1919 |  | 10130 |  |  |  | 전압 # | 1919 |  | 12434 |  |  |  | A상 전류 # | 1919 |  | 14738 |  |  |  | B상 전류 # | 1919 |  | 17042 |  |  |  | C상 전류 # | 1919
3219 |  |  |  | Trip coil 1 전류 # | 1920 |  | 5523 |  |  |  | Trip coil 2 전류 # | 1920 |  | 7827 |  |  |  | Close coil 전류 # | 1920 |  | 10131 |  |  |  | 전압 # | 1920 |  | 12435 |  |  |  | A상 전류 # | 1920 |  | 14739 |  |  |  | B상 전류 # | 1920 |  | 17043 |  |  |  | C상 전류 # | 1920
3220 | 0x03 | R | 64 | Trip coil 1 전류 # | 1921 | 16-bit unsigned integer | 5524 | 0x03 | R | 64 | Trip coil 2 전류 # | 1921 | 16-bit unsigned integer | 7828 | 0x03 | R | 64 | Close coil 전류 # | 1921 | 16-bit unsigned integer | 10132 | 0x03 | R | 128 | 전압 # | 1921 | 16-bit signed integer | 12436 | 0x03 | R | 128 | A상 전류 # | 1921 | 16-bit signed integer | 14740 | 0x03 | R | 128 | B상 전류 # | 1921 | 16-bit signed integer | 17044 | 0x03 | R | 64 | C상 전류 # | 1921 | 16-bit signed integer
3221 |  |  |  | Trip coil 1 전류 # | 1922 |  | 5525 |  |  |  | Trip coil 2 전류 # | 1922 |  | 7829 |  |  |  | Close coil 전류 # | 1922 |  | 10133 |  |  |  | 전압 # | 1922 |  | 12437 |  |  |  | A상 전류 # | 1922 |  | 14741 |  |  |  | B상 전류 # | 1922 |  | 17045 |  |  |  | C상 전류 # | 1922
3222 |  |  |  | Trip coil 1 전류 # | 1923 |  | 5526 |  |  |  | Trip coil 2 전류 # | 1923 |  | 7830 |  |  |  | Close coil 전류 # | 1923 |  | 10134 |  |  |  | 전압 # | 1923 |  | 12438 |  |  |  | A상 전류 # | 1923 |  | 14742 |  |  |  | B상 전류 # | 1923 |  | 17046 |  |  |  | C상 전류 # | 1923
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
3281 |  |  |  | Trip coil 1 전류 # | 1982 |  | 5585 |  |  |  | Trip coil 2 전류 # | 1982 |  | 7889 |  |  |  | Close coil 전류 # | 1982 |  | 10193 |  |  |  | 전압 # | 1982 |  | 12497 |  |  |  | A상 전류 # | 1982 |  | 14801 |  |  |  | B상 전류 # | 1982 |  | 17105 |  |  |  | C상 전류 # | 1982
3282 |  |  |  | Trip coil 1 전류 # | 1983 |  | 5586 |  |  |  | Trip coil 2 전류 # | 1983 |  | 7890 |  |  |  | Close coil 전류 # | 1983 |  | 10194 |  |  |  | 전압 # | 1983 |  | 12498 |  |  |  | A상 전류 # | 1983 |  | 14802 |  |  |  | B상 전류 # | 1983 |  | 17106 |  |  |  | C상 전류 # | 1983
3283 |  |  |  | Trip coil 1 전류 # | 1984 |  | 5587 |  |  |  | Trip coil 2 전류 # | 1984 |  | 7891 |  |  |  | Close coil 전류 # | 1984 |  | 10195 |  |  |  | 전압 # | 1984 |  | 12499 |  |  |  | A상 전류 # | 1984 |  | 14803 |  |  |  | B상 전류 # | 1984 |  | 17107 |  |  |  | C상 전류 # | 1984
3284 | 0x03 | R | 64 | Trip coil 1 전류 # | 1985 | 16-bit unsigned integer | 5588 | 0x03 | R | 64 | Trip coil 2 전류 # | 1985 | 16-bit unsigned integer | 7892 | 0x03 | R | 64 | Close coil 전류 # | 1985 | 16-bit unsigned integer | 10196 | 0x03 | R | 64 | 전압 # | 1985 | 16-bit signed integer | 12500 | 0x03 | R | 64 | A상 전류 # | 1985 | 16-bit signed integer | 14804 | 0x03 | R | 64 | B상 전류 # | 1985 | 16-bit signed integer | 17108 | 0x03 | R | 64 | C상 전류 # | 1985 | 16-bit signed integer
3285 |  |  |  | Trip coil 1 전류 # | 1986 |  | 5589 |  |  |  | Trip coil 2 전류 # | 1986 |  | 7893 |  |  |  | Close coil 전류 # | 1986 |  | 10197 |  |  |  | 전압 # | 1986 |  | 12501 |  |  |  | A상 전류 # | 1986 |  | 14805 |  |  |  | B상 전류 # | 1986 |  | 17109 |  |  |  | C상 전류 # | 1986
3286 |  |  |  | Trip coil 1 전류 # | 1987 |  | 5590 |  |  |  | Trip coil 2 전류 # | 1987 |  | 7894 |  |  |  | Close coil 전류 # | 1987 |  | 10198 |  |  |  | 전압 # | 1987 |  | 12502 |  |  |  | A상 전류 # | 1987 |  | 14806 |  |  |  | B상 전류 # | 1987 |  | 17110 |  |  |  | C상 전류 # | 1987
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
3345 |  |  |  | Trip coil 1 전류 # | 2046 |  | 5649 |  |  |  | Trip coil 2 전류 # | 2046 |  | 7953 |  |  |  | Close coil 전류 # | 2046 |  | 10257 |  |  |  | 전압 # | 2046 |  | 12561 |  |  |  | A상 전류 # | 2046 |  | 14865 |  |  |  | B상 전류 # | 2046 |  | 17169 |  |  |  | C상 전류 # | 2046
3346 |  |  |  | Trip coil 1 전류 # | 2047 |  | 5650 |  |  |  | Trip coil 2 전류 # | 2047 |  | 7954 |  |  |  | Close coil 전류 # | 2047 |  | 10258 |  |  |  | 전압 # | 2047 |  | 12562 |  |  |  | A상 전류 # | 2047 |  | 14866 |  |  |  | B상 전류 # | 2047 |  | 17170 |  |  |  | C상 전류 # | 2047
3347 |  |  |  | Trip coil 1 전류 # | 2048 |  | 5651 |  |  |  | Trip coil 2 전류 # | 2048 |  | 7955 |  |  |  | Close coil 전류 # | 2048 |  | 10259 |  |  |  | 전압 # | 2048 |  | 12563 |  |  |  | A상 전류 # | 2048 |  | 14867 |  |  |  | B상 전류 # | 2048 |  | 17171 |  |  |  | C상 전류 # | 2048
3348 | 0x03 | R | 64 | Trip coil 1 전류 # | 2049 | 16-bit unsigned integer | 5652 | 0x03 | R | 64 | Trip coil 2 전류 # | 2049 | 16-bit unsigned integer | 7956 | 0x03 | R | 64 | Close coil 전류 # | 2049 | 16-bit unsigned integer | 10260 | 0x03 | R | 64 | 전압 # | 2049 | 16-bit signed integer | 12564 | 0x03 | R | 64 | A상 전류 # | 2049 | 16-bit signed integer | 14868 | 0x03 | R | 64 | B상 전류 # | 2049 | 16-bit signed integer | 17172 | 0x03 | R | 64 | C상 전류 # | 2049 | 16-bit signed integer
3349 |  |  |  | Trip coil 1 전류 # | 2050 |  | 5653 |  |  |  | Trip coil 2 전류 # | 2050 |  | 7957 |  |  |  | Close coil 전류 # | 2050 |  | 10261 |  |  |  | 전압 # | 2050 |  | 12565 |  |  |  | A상 전류 # | 2050 |  | 14869 |  |  |  | B상 전류 # | 2050 |  | 17173 |  |  |  | C상 전류 # | 2050
3350 |  |  |  | Trip coil 1 전류 # | 2051 |  | 5654 |  |  |  | Trip coil 2 전류 # | 2051 |  | 7958 |  |  |  | Close coil 전류 # | 2051 |  | 10262 |  |  |  | 전압 # | 2051 |  | 12566 |  |  |  | A상 전류 # | 2051 |  | 14870 |  |  |  | B상 전류 # | 2051 |  | 17174 |  |  |  | C상 전류 # | 2051
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
3409 |  |  |  | Trip coil 1 전류 # | 2110 |  | 5713 |  |  |  | Trip coil 2 전류 # | 2110 |  | 8017 |  |  |  | Close coil 전류 # | 2110 |  | 10321 |  |  |  | 전압 # | 2110 |  | 12625 |  |  |  | A상 전류 # | 2110 |  | 14929 |  |  |  | B상 전류 # | 2110 |  | 17233 |  |  |  | C상 전류 # | 2110
3410 |  |  |  | Trip coil 1 전류 # | 2111 |  | 5714 |  |  |  | Trip coil 2 전류 # | 2111 |  | 8018 |  |  |  | Close coil 전류 # | 2111 |  | 10322 |  |  |  | 전압 # | 2111 |  | 12626 |  |  |  | A상 전류 # | 2111 |  | 14930 |  |  |  | B상 전류 # | 2111 |  | 17234 |  |  |  | C상 전류 # | 2111
3411 |  |  |  | Trip coil 1 전류 # | 2112 |  | 5715 |  |  |  | Trip coil 2 전류 # | 2112 |  | 8019 |  |  |  | Close coil 전류 # | 2112 |  | 10323 |  |  |  | 전압 # | 2112 |  | 12627 |  |  |  | A상 전류 # | 2112 |  | 14931 |  |  |  | B상 전류 # | 2112 |  | 17235 |  |  |  | C상 전류 # | 2112
3412 | 0x03 | R | 64 | Trip coil 1 전류 # | 2113 | 16-bit unsigned integer | 5716 | 0x03 | R | 64 | Trip coil 2 전류 # | 2113 | 16-bit unsigned integer | 8020 | 0x03 | R | 64 | Close coil 전류 # | 2113 | 16-bit unsigned integer | 10324 | 0x03 | R | 64 | 전압 # | 2113 | 16-bit signed integer | 12628 | 0x03 | R | 64 | A상 전류 # | 2113 | 16-bit signed integer | 14932 | 0x03 | R | 64 | B상 전류 # | 2113 | 16-bit signed integer | 17236 | 0x03 | R | 64 | C상 전류 # | 2113 | 16-bit signed integer
3413 |  |  |  | Trip coil 1 전류 # | 2114 |  | 5717 |  |  |  | Trip coil 2 전류 # | 2114 |  | 8021 |  |  |  | Close coil 전류 # | 2114 |  | 10325 |  |  |  | 전압 # | 2114 |  | 12629 |  |  |  | A상 전류 # | 2114 |  | 14933 |  |  |  | B상 전류 # | 2114 |  | 17237 |  |  |  | C상 전류 # | 2114
3414 |  |  |  | Trip coil 1 전류 # | 2115 |  | 5718 |  |  |  | Trip coil 2 전류 # | 2115 |  | 8022 |  |  |  | Close coil 전류 # | 2115 |  | 10326 |  |  |  | 전압 # | 2115 |  | 12630 |  |  |  | A상 전류 # | 2115 |  | 14934 |  |  |  | B상 전류 # | 2115 |  | 17238 |  |  |  | C상 전류 # | 2115
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
3473 |  |  |  | Trip coil 1 전류 # | 2174 |  | 5777 |  |  |  | Trip coil 2 전류 # | 2174 |  | 8081 |  |  |  | Close coil 전류 # | 2174 |  | 10385 |  |  |  | 전압 # | 2174 |  | 12689 |  |  |  | A상 전류 # | 2174 |  | 14993 |  |  |  | B상 전류 # | 2174 |  | 17297 |  |  |  | C상 전류 # | 2174
3474 |  |  |  | Trip coil 1 전류 # | 2175 |  | 5778 |  |  |  | Trip coil 2 전류 # | 2175 |  | 8082 |  |  |  | Close coil 전류 # | 2175 |  | 10386 |  |  |  | 전압 # | 2175 |  | 12690 |  |  |  | A상 전류 # | 2175 |  | 14994 |  |  |  | B상 전류 # | 2175 |  | 17298 |  |  |  | C상 전류 # | 2175
3475 |  |  |  | Trip coil 1 전류 # | 2176 |  | 5779 |  |  |  | Trip coil 2 전류 # | 2176 |  | 8083 |  |  |  | Close coil 전류 # | 2176 |  | 10387 |  |  |  | 전압 # | 2176 |  | 12691 |  |  |  | A상 전류 # | 2176 |  | 14995 |  |  |  | B상 전류 # | 2176 |  | 17299 |  |  |  | C상 전류 # | 2176
3476 | 0x03 | R | 64 | Trip coil 1 전류 # | 2177 | 16-bit unsigned integer | 5780 | 0x03 | R | 64 | Trip coil 2 전류 # | 2177 | 16-bit unsigned integer | 8084 | 0x03 | R | 64 | Close coil 전류 # | 2177 | 16-bit unsigned integer | 10388 | 0x03 | R | 64 | 전압 # | 2177 | 16-bit signed integer | 12692 | 0x03 | R | 64 | A상 전류 # | 2177 | 16-bit signed integer | 14996 | 0x03 | R | 64 | B상 전류 # | 2177 | 16-bit signed integer | 17300 | 0x03 | R | 64 | C상 전류 # | 2177 | 16-bit signed integer
3477 |  |  |  | Trip coil 1 전류 # | 2178 |  | 5781 |  |  |  | Trip coil 2 전류 # | 2178 |  | 8085 |  |  |  | Close coil 전류 # | 2178 |  | 10389 |  |  |  | 전압 # | 2178 |  | 12693 |  |  |  | A상 전류 # | 2178 |  | 14997 |  |  |  | B상 전류 # | 2178 |  | 17301 |  |  |  | C상 전류 # | 2178
3478 |  |  |  | Trip coil 1 전류 # | 2179 |  | 5782 |  |  |  | Trip coil 2 전류 # | 2179 |  | 8086 |  |  |  | Close coil 전류 # | 2179 |  | 10390 |  |  |  | 전압 # | 2179 |  | 12694 |  |  |  | A상 전류 # | 2179 |  | 14998 |  |  |  | B상 전류 # | 2179 |  | 17302 |  |  |  | C상 전류 # | 2179
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
3537 |  |  |  | Trip coil 1 전류 # | 2238 |  | 5841 |  |  |  | Trip coil 2 전류 # | 2238 |  | 8145 |  |  |  | Close coil 전류 # | 2238 |  | 10449 |  |  |  | 전압 # | 2238 |  | 12753 |  |  |  | A상 전류 # | 2238 |  | 15057 |  |  |  | B상 전류 # | 2238 |  | 17361 |  |  |  | C상 전류 # | 2238
3538 |  |  |  | Trip coil 1 전류 # | 2239 |  | 5842 |  |  |  | Trip coil 2 전류 # | 2239 |  | 8146 |  |  |  | Close coil 전류 # | 2239 |  | 10450 |  |  |  | 전압 # | 2239 |  | 12754 |  |  |  | A상 전류 # | 2239 |  | 15058 |  |  |  | B상 전류 # | 2239 |  | 17362 |  |  |  | C상 전류 # | 2239
3539 |  |  |  | Trip coil 1 전류 # | 2240 |  | 5843 |  |  |  | Trip coil 2 전류 # | 2240 |  | 8147 |  |  |  | Close coil 전류 # | 2240 |  | 10451 |  |  |  | 전압 # | 2240 |  | 12755 |  |  |  | A상 전류 # | 2240 |  | 15059 |  |  |  | B상 전류 # | 2240 |  | 17363 |  |  |  | C상 전류 # | 2240
3540 | 0x03 | R | 64 | Trip coil 1 전류 # | 2241 | 16-bit unsigned integer | 5844 | 0x03 | R | 64 | Trip coil 2 전류 # | 2241 | 16-bit unsigned integer | 8148 | 0x03 | R | 64 | Close coil 전류 # | 2241 | 16-bit unsigned integer | 10452 | 0x03 | R | 64 | 전압 # | 2241 | 16-bit signed integer | 12756 | 0x03 | R | 64 | A상 전류 # | 2241 | 16-bit signed integer | 15060 | 0x03 | R | 64 | B상 전류 # | 2241 | 16-bit signed integer | 17364 | 0x03 | R | 64 | C상 전류 # | 2241 | 16-bit signed integer
3541 |  |  |  | Trip coil 1 전류 # | 2242 |  | 5845 |  |  |  | Trip coil 2 전류 # | 2242 |  | 8149 |  |  |  | Close coil 전류 # | 2242 |  | 10453 |  |  |  | 전압 # | 2242 |  | 12757 |  |  |  | A상 전류 # | 2242 |  | 15061 |  |  |  | B상 전류 # | 2242 |  | 17365 |  |  |  | C상 전류 # | 2242
3542 |  |  |  | Trip coil 1 전류 # | 2243 |  | 5846 |  |  |  | Trip coil 2 전류 # | 2243 |  | 8150 |  |  |  | Close coil 전류 # | 2243 |  | 10454 |  |  |  | 전압 # | 2243 |  | 12758 |  |  |  | A상 전류 # | 2243 |  | 15062 |  |  |  | B상 전류 # | 2243 |  | 17366 |  |  |  | C상 전류 # | 2243
………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | ………… | [6 empty] | …………
3601 |  |  |  | Trip coil 1 전류 # | 2302 |  | 5905 |  |  |  | Trip coil 2 전류 # | 2302 |  | 8209 |  |  |  | Close coil 전류 # | 2302 |  | 10513 |  |  |  | 전압 # | 2302 |  | 12817 |  |  |  | A상 전류 # | 2302 |  | 15121 |  |  |  | B상 전류 # | 2302 |  | 17425 |  |  |  | C상 전류 # | 2302
3602 |  |  |  | Trip coil 1 전류 # | 2303 |  | 5906 |  |  |  | Trip coil 2 전류 # | 2303 |  | 8210 |  |  |  | Close coil 전류 # | 2303 |  | 10514 |  |  |  | 전압 # | 2303 |  | 12818 |  |  |  | A상 전류 # | 2303 |  | 15122 |  |  |  | B상 전류 # | 2303 |  | 17426 |  |  |  | C상 전류 # | 2303
3603 |  |  |  | Trip coil 1 전류 # | 2304 |  | 5907 |  |  |  | Trip coil 2 전류 # | 2304 |  | 8211 |  |  |  | Close coil 전류 # | 2304 |  | 10515 |  |  |  | 전압 # | 2304 |  | 12819 |  |  |  | A상 전류 # | 2304 |  | 15123 |  |  |  | B상 전류 # | 2304 |  | 17427 |  |  |  | C상 전류 # | 2304