## Blocker DataModel
data model
| name | CDC | explanation | LU | MU
| mod | INC |  | ○ | ○
| Beh | INS |  | ○ | ○
| Health | INS |  | ○ | ○
| NamPlt | LPL |  | ○ | ○
| EEName | DPL |  | × | ○
Status
| ColOpn | SPS | Trip coil open command | ○ | ○ | Is there no input coil input command?
| AbrAlm | SPS | Contact wear alarm | × | ○ | What is the criterion for determining contact wear?
| AbrWrn | SPS | Contact wear alarm | × | ○
| OpTmAlm | SPS | switch operation timeout | ○ | ○ | Jibon: Explain OpTmAlm
| ColAlm | SPS | coil alarm | × | ○ | What is Coil Alarm? Is the coil current exceeding the standard value?
| OpCntAlm | SPS | Alarm level exceeded operation count | × | ○
| OpCntWrn | SPS | Warning level exceeded operation count | × | ○
| OpTmWrn | SPS | Warning level operation time | × | ○
| OpTmh | INS | installation time setting time | × | ○ | What is the installation time setting time?
| EvtTransF | INS | event occurrence flag | ○ | ○
| RsOpCnt | ING | Breaker operation count | ○ | ○
| MoDevComF | SPS | communication status | ○ | ○ | Communication status with ACQ?
| MoDevFlt | SPS | hardware fault | ○ | ○ | H/W fault status of ACQ?
| CbAlm | INS | CB Alarm | × | ○
Measurands
| AccAbr | MV | cumulative wear amount | ○ | ○ | How do you know the amount of wear?
| SwA | MV | Current cut-off current amount | ○ | ○
| ActAbr | MV | recent wear | ○ | ○ | How do you know the amount of wear?
| AuxSwTmOpn | MV | Open auxiliary switch timing | ○ | ○
| AuxSwTmCls | MV | Closing auxiliary switch timing | ○ | ○
| RctTmOpn | MV | opening response time | ○ | ○
| RctTmCls | MV | input reaction time | ○ | ○
| OpSpdOpn | MV | opening action speed | ○ | ○ | What does speed mean? Is there such a thing as moving distance?
| OpSpdCls | MV | Closing motion speed | ○ | ○ | What does speed mean? Is there such a thing as moving distance?
| OpTmOpn | MV | open operation time | ○ | ○
| OpTmCls | MV | Closing operation time | ○ | ○
| Stk | MV | contact point | ○ | ○ | What is the measured value of "contact contact"?
| OvStkOpn | MV | openness and contact | ○ | ○ | What is the measurement of "open and contact"?
| OvStkCls | MV | closure and contact | ○ | ○ | What is the metric called "closure and contact"?
| ColA | MV | coil current | ○ | ○
| Tmp | MV | temperature | ○ | ○ | temperature?
| ColV | MV | coil voltage | ○ | ○ | What kind of measured value is "coil voltage"? Integral value of coil current?
| ClsColA | MV | Current input coil current | ○ | ○
| OpnColA | MV | Current amount of current blocking coil | ○ | ○
| BctA | MV | Bus current A phase | ○ | ○
| BctB | MV | Bus current phase B | ○ | ○
| BctCs | MV | Bus current phase C | ○ | ○
Settings
| AbrAlmLev | ASG | wear alarm set point | × | ○
| AbrWrnLev | ASG | Wear warning set point | × | ○
| OpAlmTmh | ING | Operating time alarm set point | × | ○
| OpWrnTmh | ING | Operating time warning set point | × | ○
| OpAlmNum | ING | Operation count alarm set point | × | ○
| OpWrnNum | ING | Operation count warning set point | × | ○

## BlockerDataSet
DataSet
|  | Local Unit → Diagnosis Unit | Diagnosis unit →HMIserver
| Status | EvtTransF(event occursFlag) | EvtTransF(event occursFlag)
|  | RsOpCnt (number of operations) | CbAlm (alarm occurs)
|  | MoDevComF (communication status) | RsOpCnt (number of operations)
|  | MoDevFlt (H/W Fault) | MoDevComF (communication status)
MoDevFlt (H/W Fault)

## Blocker FileFormat
File Format
| division | Size |  | type | detail | note |  |  |  |  | LU | MU
(Bytes)
| ②CBCM | 98 | 1 | uint8 | event type | Trip=0x55, Close=0xAA |  |  |  |  | O | O
|  | (information) | 4 | uint32 | event time | year,month,Day,city,minute,candle(UTC+9) |  |  |  |  | O | O
| 98+29952 |  | 4 | uint32 | event time | msec (yes:value200silver200msrecognized as) |  |  |  |  | O | O
| 30050 |  | 1 | uint8 | alert level(uint8) | Cause when an alarm occurs(DiagnosisUnitAlarm as a result of this diagnosisEnumfill with value) |  |  |  |  | X | O
|  |  | 4 | float | contact duty A | breaking currentAmain) One |  |  |  |  | X | O
|  |  | 4 | float | contact duty B | breaking currentBmain) 2 |  |  |  |  | X | O
|  |  | 4 | float | contact duty C | breaking currentCmain) 3 |  |  |  |  | X | O
|  |  | 4 | float | accum c. duty A | Cumulative breaking currentAmain) One |  |  |  |  | X | O
|  |  | 4 | float | accum c. duty B | Cumulative breaking currentBmain) 2 |  |  |  |  | X | O
|  |  | 4 | float | accum c. duty C | Cumulative breaking currentCmain) 3 |  |  |  |  | X | O
|  |  | 4 | float | T1coil integral value | ∫ABS(i)dt(AS) (= TripProfileArea: sec) |  |  |  |  | X | O | Are you trying to get the voltage by integrating the absolute value of the current?
|  |  | 4 | float | T1coil max current | peakelectric current(= TripCoilPeak) |  |  |  |  | X | O
|  |  | 4 | float | T1coil girl time | female coil start(Increase)~end(descent)time to point |  |  |  |  | X | O
[6 empty] | (= TripCurrflow: msec) |  |  |  |  | X | O
|  |  | 4 | float | T2coil integral value | ∫ABS(i)dt(AS) (= TripProfileArea: sec) |  |  |  |  | X | O | Are you trying to get the voltage by integrating the absolute value of the current?
|  |  | 4 | float | T2coil max current | peakelectric current(= TripCoilPeak) |  |  |  |  | X | O
|  |  | 4 | float | T2coil girl time | female coil start(Increase)~end(descent)time to point |  |  |  |  | X | O
[6 empty] | (= TripCurrflow: msec) |  |  |  |  | X | O
|  |  | 4 | float | Ccoil integral value | ∫ABS(i)dt(AS) (= CloseProfileArea : sec) |  |  |  |  | X | O | Are you trying to get the voltage by integrating the absolute value of the current?
|  |  | 4 | float | Ccoil max current | peakelectric current(= CloseCoilPeak) |  |  |  |  | X | O
|  |  | 4 | float | Ccoil girl time | female coil start(Increase)~end(descent)time to point |  |  |  |  | X | O
[6 empty] | (= CloseCurrflow: msec) |  |  |  |  | X | O
|  |  | 4 | float | Acontact operation time | girl time~ATime until contact change |  |  |  |  | X | O
|  |  | 4 | float | Bcontact operation time | girl time~BTime until contact change |  |  |  |  | X | O
|  |  | 4 | float | Block by phase/ | unit: msecmain) One (Trip or Close time) |  |  |  |  | X | O
[5 empty] | input time(Aaward) | [5 empty] | X | O
|  |  | 4 | float | Block by phase/ | unit: msecmain) 2 (Trip or Close time) |  |  |  |  | X | O
[5 empty] | input time(Baward) | [5 empty] | X | O
|  |  | 4 | float | Block by phase/ | unit: msecmain) 3 (Trip or Close time) |  |  |  |  | X | O
[5 empty] | input time(Caward) | [5 empty] | X | O
|  |  | 4 | uint32 | OpCnt | circuit breaker operation count(Tripin motion) |  |  |  |  | X | O
|  |  | 2 | uint16 | smpPerCyc | sampling number(128fixed value) |  |  |  |  | X | O
|  | 98 | 2 | uint16 | cycCnt | cyclenumber( 18fixed value) |  |  |  |  | X | O
|  | 29952 | 4608 | uint16 | Trip1_CoilCurrent | waveform data(T1-Coil) |  |  |  |  | O | O | = sizeof(uint16) * 128 samples/cycle * 18 cycles
|  | (waveform) | 4608 | uint16 | Trip2_CoilCurrent | waveform data(T2-Coil) |  |  |  |  | O | O | = sizeof(uint16) * 128 samples/cycle * 18 cycles
|  |  | 4608 | uint16 | CloseCoilCurrent | waveform data(C-Coil) |  |  |  |  | O | O | = sizeof(uint16) * 128 samples/cycle * 18 cycles
|  |  | 4608 | uint16 | PhaseCurrentA | waveform data(Aaward)main) One |  |  |  |  | O | O
[6 empty] | (2byte * 18cycle * 128sample = 4608) |  |  |  |  | O | O
|  |  | 4608 | uint16 | PhaseCurrentB | waveform data(Baward)main) 2 |  |  |  |  | O | O
[6 empty] | (2byte * 18cycle * 128sample = 4608) |  |  |  |  | O | O
|  |  | 4608 | uint16 | PhaseCurrentC | waveform data(Caward)main) 3 |  |  |  |  | O | O
[6 empty] | (2byte * 18cycle * 128sample = 4608) |  |  |  |  | O | O
|  |  | 2304 | char | InitiateAndContact | waveform data(A/BContact, ON=1, OFF=0) |  |  |  |  | O | O | = sizeof(char) * 128 samples/cycle * 18 cycles
[6 empty] | (1byte * 18cycle * 128sample = 2304) |  |  |  |  | O | O
[6 empty] | 7 bits (MSB) | 6bit | ... | 1 bit | 0bit | O | O
| 30050 | 29952 |  |  |  | - | - | ... | bContact | aContact | O | O
| main) One : | -3phase batch type: Atreat as award
- 3phase separated:Setting information values ​​for each phase(A, BorCphase value information)
| main) 2 : | -3phase batch type:Btreat as award- 3phase separated: NULL
| main) 3 : | -3phase batch type:Ctreat as award- 3phase separated: NULL

## Gas in OilDataModel
data model
| name | CDC | explanation | LU | MU | note
| mod | INC |  | ○ | ○
| Beh | INS |  | ○ | ○
| Health | INS |  | ○ | ○ | sensor status
| NamPlt | LPL |  | ○ | ○
| EEName | DPL |  | × | ○
Status
| InsAlm | SPS | insulating oil alarm | × | ○
| H2Alm | SPS | H2 Alarm | × | ○ | hydrogen
| N2Alm | SPS | N2 Alarm | × | ○ | nitrogen
| O2Alm | SPS | O2 Alarm | × | ○ | Oxygen
| C2H2Alm | SPS | C2H2 Alarm | × | ○ | acetylene
| CH4Alm | SPS | CH4 Alarm | × | ○ | methane
| C2H6Alm | SPS | C2H6 Alarm | × | ○ | ethane
| C2H4Alm | SPS | C2H4 Alarm | × | ○ | ethylene
| COAlm | SPS | CO Alarm | × | ○ | carbon monoxide
| CO2Alm | SPS | CO2 Alarm | × | ○ | carbon dioxide
| MstAlm | SPS | Moisture Alarm | × | ○ | moisture(H2O)
| C3H8Alm | SPS | C3H8 Alarm | × | ○ | propane
| MoDevComF | SPS | communication status | ○ | ○
| MoDevFlt | SPS | hardware fault | ○ | ○
| DgaAlm | INS | DGA Alarm | × | ○
Measurands
| Tmp | MV | H2ppm | ○ | ○ | insulating oil temperature
| Lev | MV | N2ppm | ○ | ○ | Insulation oil level
| Pres | MV | O2ppm | ○ | ○ | insulating oil pressure
| H2Oppm | MV | H2O ppm | ○ | ○ | water
| H2ppm | MV | H2ppm | ○ | ○ | hydrogen
| N2ppm | MV | N2ppm | ○ | ○ | nitrogen
| COppm | MV | CO ppm | ○ | ○ | carbon monoxide
| CO2ppm | MV | CO2 ppm | ○ | ○ | carbon dioxide
| CH4ppm | MV | CH4 ppm | ○ | ○ | methane
| C2H2ppm | MV | C2H2 ppm | ○ | ○ | acetylene
| C2H4ppm | MV | C2H4 ppm | ○ | ○ | ethylene
| C2H6ppm | MV | C2H6 ppm | ○ | ○ | ethane
| O2ppm | MV | O2ppm | ○ | ○ | Oxygen
| C3H8ppm | MV | C3H8 ppm | O | O | propane
Settings
| H2AlmSpt | ASG | H2 Alarm set-point | × | ○ | hydrogen
| N2AlmSpt | ASG | N2 Alarm set-point | × | ○ | nitrogen
| O2AlmSpt | ASG | O2 Alarm set-point | × | ○ | Oxygen
| C2H2AlmSpt | ASG | C2H2 Alarm set-point | × | ○ | acetylene
| CH4AlmSpt | ASG | CH4 Alarm set-point | × | ○ | methane
| C2H6AlmSpt | ASG | C2H6 Alarm set-point | × | ○ | ethane
| C2H4AlmSpt | ASG | C2H4 Alarm set-point | × | ○ | ethylene
| COAlmSpt | ASG | CO Alarm set-point | × | ○ | carbon monoxide
| CO2AlmSpt | ASG | CO2 Alarm set-point | × | ○ | carbon dioxide
| MstAlmSpt | ASG | Moisture Alarm set-point | × | ○ | moisture
| C3H8AlmSpt | ASG | C3H8 Alarm set-point | X | O | propane

## Gas in Oil DataSet
DataSet
|  | Local Unit → Diagnosis Unit | Diagnosis unit →HMIserver
| Status | MoDevComF | DgaAlm
|  | MoDevFlt | H2Alm
N2Alm
O2Alm
C2H2Alm
CH4Alm
C2H6Alm
C2H4Alm
COAlm
COAlm
MstAlm
| Measurands | H2ppm | H2ppm
|  | N2ppm | N2ppm
|  | O2ppm | O2ppm
|  | C2H2ppm | C2H2ppm
|  | CH4ppm | CH4ppm
|  | C2H6ppm | C2H6ppm
|  | C2H4ppm | C2H4ppm
|  | COppm | COppm
|  | COppm | COppm
|  | H2Oppm | H2Oppm

## OLTC DataModel
data model
| name | CDC | explanation | LU | MU
| mod | INC |  | ○ | ○
| Beh | INS |  | ○ | ○
| Health | INS |  | ○ | ○
| NamPlt | LPL |  | ○ | ○
| EEName | DPL |  | × | ○
Status
| OilFil | SPS | Oil filter operation status | ○ | ○ | unused now?
| MotDrvBlk | SPS | Driving motor overcurrent cut off | ○ | ○ | How do you know it's blocking overcurrent? The contacts coming from the motor do not
| VacCelAlm | SPS | Decompression cell circuit status | ○ | ○ | Decompression cell circuit?
| OilFilTr | SPS | oil filter trip | ○ | ○ | unused now?
| MotDrvAAlm | SPS | Drive motor current alarm | × | ○
| MotDrvAWrn | SPS | Drive motor current alarm | × | ○
| TorqAlm | SPS | Drive motor torque alarm | × | ○
| TorqWrn | SPS | Drive motor torque alarm | × | ○
| OpDurAlm | SPS | LTCoperating time alarm | × | ○
| OpDurWrn | SPS | LTCoperating time alarm | × | ○
| OpCntAlm | SPS | LTCMotion count alarm | × | ○
| OpCntWrnl | SPS | LTCMotion count alarm | × | ○
| ArbPrtAlm | SPS | LTCwear alarm | × | ○
| ArbPrtWrn | SPS | LTCwear alarm | × | ○
| OilTmpDifAlm | SPS | LTC-Transformer oil temperature difference alarm | × | ○ | unused now?
| OilFiltCnt | INS | Number of oil filter filtration | ○ | ○ | unused now?
| OilFilmCntAlm | SPS | Oil filter oil filtration count alarm | × | ○ | unused now?
| OilFilCntWrn | SPS | Oil Filter Number of Oil Filters Warning | × | ○ | unused now?
| EvtTransF | INS | event occurrence flag | ○ | ○
| RsOpCnt | ING | LTCnumber of operations | ○ | ○
| MoDevComF | SPS | communication status | ○ | ○
| MoDevFlt | SPS | hardware fault | ○ | ○
| LtcAlm | INS | LTC Alarm | × | ○
Measurands
| Torq | MV | drive motor torque | ○ | ○ | How to measure drive motor torque?
| MotDrvA | MV | drive motor current | ○ | ○
| AbrPrt | MV | LTCdegree of wear | ○ | ○ | How do you measure LTC wear?
| OpDur | MV | LTCoperating time | ○ | ○
| OilTmpDif | MV | LTC-Transformer temperature difference | ○ | ○ | unused now?
| OutTmp | MV | outside temperature | ○ | ○
| MotDrvAphsA | MV | driving motorAphase current | ○ | ○
| MotDrvAphsB | MV | driving motorBphase current | ○ | ○
| MotDrvAphsC | MV | driving motorCphase current | ○ | ○
| OilFiltmp | MV | insulating oil temperature | ○ | ○ | unused now?
| OilFilBar | MV | insulating oil pressure | ○ | ○ | unused now?
| OilFilmst | MV | Moisture content of insulating oil | ○ | ○ | unused now?
Controls
| OpCntRs | INC | LTCnumber of operations | ○ | ○
Settings
| MDAAlmLev | ASG | Drive Motor Current Alarm Threshold | × | ○
| MDAWrnLev | ASG | Drive motor current warning threshold | × | ○
| TorqAlmLev | ASG | Drive Motor Torque Alarm Threshold | × | ○
| TorqWrnLev | ASG | Drive motor torque warning threshold | × | ○
| OpDurAlmLev | ASG | LTCOperating Time Alarm Threshold | × | ○ | Is there no setting of the operation count alarm threshold?
| OpDurWrnLev | ASG | LTCUptime warning threshold | × | ○ | Is there any setting for the number of operation warning threshold?
OLTC monitoring is based on receiving data at every OLTC operation.

## OLTC DataSets
DataSet
|  | Local Unit → Diagnosis Unit | implementation | Diagnosis unit →HMIserver
| Status | EvtTransF(event occursFlag) |  | EvtTransF(event occursFlag)
LTCAlm (alarm occurs)
| Measurands | MotDrvAphsA (motorAphase current) | OK | MotDrvAphsA (motorAphase current)
|  | MotDrvAphsB (motorBphase current) | OK | MotDrvAphsB (motorBphase current)
|  | MotDrvAphsC (motorCphase current) | OK | MotDrvAphsC (motorCphase current)
|  | OpDur (Last event operating time) |  | OpDur (Last event operating time)
|  | OilFilTmp(oil temperature) | unused | OilFilTmp(oil temperature)
|  | OilFilBar(Hydraulics) | unused | OilFilBar(Hydraulics)
|  | OilFilmst(Oil and moisture content) | unused | OilFilmst(Oil and moisture content)
|  | OutTmp(outside temperature) | OK | OutTmp(outside temperature)

## OLTC FileFormat
File Format
| Size |  | detail | note
(Bytes)
| 691230 | 4 | creation time(uint32) | Drive motor operation event occurrence time(UTC+9) | information reception time
|  | 1 | alert level(uint32) | Null | 0
|  | 4 | operating time(int32) | msec | measured time value
|  | 4 | number of moves(int32) | Number of drive motor operations | ?
|  | 4 | max current(float) |  | ?
|  | 4 | average current(float) |  | ?
|  | 4 | phase number(uint32) | 128 sample | 128
|  | 1 | Single data length(char) | 2 | 2
|  | 4 | number of data samples(uint32) | MAX: 15sec * 60cycle * 128sample=115200 | 115200
|  | 230400 | Aphase current(int16) | 2 bytes * 128 samples * 60 cycles * 15 sec | 115200 number of current values
|  | 230400 | Bphase current(int16) | 2 bytes * 128 samples * 60 cycles * 15 sec | 115200 number of current values
|  | 230400 | Cphase current(int16) | 2 bytes * 128 samples * 60 cycles * 15 sec | 115200 number of current values

## Additional information related
Modify the DevType of the existing SPDC model
name | CDC | explanation | LU | MU | note
DevType | INS | device type | O | O | 1:GIS 2:Mtr 3:Cable 4:OLTC 999:Noise
file name add waveform code
LN | FileType | Code
SPDCs (OLTCs) | Realtime | 70
| Trend | 71
| Event | 72
Does OLTC partial discharge continue?

## Bushing DataModel
data model
| name | CDC | explanation | LU | MU
| mod | INC |  | ○ | ○
| Beh | INS |  | ○ | ○
| Health | INS |  | ○ | ○
| NamPlt | LPL |  | ○ | ○
| EEName | DPL |  | × | ○
Status
| BshAlm | INS | bushing alarm | × | ○
| EvtTransF | INS | event occurrence flag | ○ | ○
| RTTransF | INS | Real-time file occurrence flag | ○ | ○
| MoDevComF | SPS | communication status | ○ | ○
| MoDevFlt | SPS | hardware fault | ○ | ○
Measurands
| React | MV | Capacitanceratio | ○ | ○ | what's the ratio? Is it the ratio of the capacitance measurement value to the capacitance set value below?
| AbsReact | MV | Capacitancevalue | ○ | ○
| LosFact | MV | loss factor | ○ | ○ | Dissipation factor (tan delta)?
| Vol | MV | voltage value | ○ | ○
| DisplA | MV | displacement current | ○ | ○ | displacement current? Like a capacitor, which is the current flowing between the two electrodes? How to measure?
| LeakA | MV | leakage current value | ○ | ○
| LeakAphs | MV | Leakage current phase | ○ | ○
| Volphs | MV | voltage phase | ○ | ○
| PF | MV | power factor | ○ | ○
| UnblA | MV | unbalanced current | ○ | ○
| UnblAphs | MV | unbalanced current phase | ○ | ○
Settings
| RefReact | ASG | Capacitanceset value | × | ○
| RefPF | ASG | power factor setpoint | × | ○
| RefV | ASG | voltage setpoint | × | ○

## Bushing DataSet
DataSet
|  | Local Unit → Diagnosis Unit | implementation | Diagnosis unit →HMIserver
| Status | EvtTransF(event occursFlag) |  | EvtTransF(event occursFlag)
|  | RsOpCnt (number of operations) |  | BSHAlm (alarm occurs)
|  | MoDevComF (communication status) |  | RsOpCnt (number of operations)
|  | MoDevFlt (H/W Fault) |  | MoDevComF (communication status)
MoDevFlt (H/W Fault)
| Measurands | React (capacitance ratio) |  | React (capacitance ratio)
|  | AbsReact(Capacitance value) | OK | AbsReact(Capacitance value)
|  | LosFact (loss factor) | OK | LosFact (loss factor)
|  | Vol (Voltage) | OK | Vol (Voltage)
|  | DisplA (displacement current) | OK | DisplA (displacement current)
|  | LeakA (leakage current) | OK | LeakA (leakage current)
|  | LeakAphs (leakage current phase) | OK | LeakAphs (leakage current phase)
|  | Volphs (voltage phase) | OK | Volphs (voltage phase)
|  | PF (power factor) | OK | PF (power factor)
|  | UnblA (unbalanced current) | OK | UnblA (unbalanced current)
|  | UnblAphs (unbalanced current phase) | OK | UnblAphs (unbalanced current phase)