## Slide 1: breakeroperating characteristics analyzer(ACQ) circuit analysis
2021.12.02
Senion Co., Ltd.
Translated from Korean to English - www.onlinedoctranslator.com

## Slide 2: index
ACQdevelopment request
ACQBlock Diagram and Circuit Construction
Review the results

## Slide 3: ACQDevelopment request
H/Wspecification
division | item | specification | note
conditions of use | ambient temperature | -25 to 55 | 
H/W specification | Voltage | 110/V 1ch | 
 | load current | 1.66mA 3ch(A,B,C) | CTOneSecondary side rating5A
 | coil current(DC) | ±4V 3ch(Close1ch, Trip 2ch) | CTOneSecondary side rating DC 0~30A
 | everyone | DC48V | PoE
 | DI | 2ch | CBContact(A, B)
 | visual information | RTC | 
 | LED | 4ea | PW, Run, Alarm, Error
communication | Ethernet | 100Base-T | everyone(PoE)Combined use
 | RS-232C | for maintenance | Consolefunction
division | item | specification | note
conditions of use | ambient temperature | -25 to 55 | 
H/W specification | Voltage |  | 
 | load current | 1.66mA 3ch(A,B,C) | CTOneSecondary side rating5A
 | coil current(DC) | ±4V 3ch(Close1ch, Trip 2ch) | CTOneSecondary side rating DC 0~30A
 | everyone | DC48V | PoE
 | DI | 2ch | CBContact(A, B)
 | visual information | RTC | 
 | LED | 4ea | PW, Run, Alarm, Error
communication | Ethernet | 100Base-T | everyone(PoE)Combined use
 | RS-232C | for maintenance | Consolefunction

## Slide 4: ACQblock diagram
PT 1ch
load current 3ch
coil current 3ch
CBContact2ch
16bit ADC
temperature Senser
OutWatchdog
non-volatileMemory
C28line
DSPprocessor
for maintenance
power andEthernet

## Slide 5: ACQcircuit configuration(MAIN)
C28line
DSP Coreprocessor
200Mhz
Wiznet, MRAM
address pin
Wiznet, MRAM,ADC
data pin
DI 2ch GPIO
LED 4ea
ADC,MRAM
control pin
Reset time out140ms
Watchdog time out 1.6s
JTAG

## Slide 6: Ethernet(WiznetW5300)
PoE Circuit
RJ45pin
1:TXD+2:TXD-
3: RXD+6:RXD-
4,5:PoE+ 7,8:PoE-
Need to inquire what intention it was designed for
Linksignal
DSP GPIOallocation required
SAFARI EMCCountermeasures
nCS4area

## Slide 7: ADC & MRAM
nCS3 ADCarea
8Chinput
16bit Data
RC LPF
ADC if it affects the inputCAPeliminate…
nCS2 MRAMarea
temperature Senser

## Slide 8: PT&Load current measurement
PT 1ch
load current3ch
ADCinput
Sallen-KeyLPF
Fc = 3.195 kHz

## Slide 9: coil current
VD=0.66
Gain = 3.56
Voltageto Frequency
Frequency to Voltage

## Slide 11: power circuit

## Slide 12: I/O andD-SUB
coil current 3ch
4pinEach connector needs to be disconnected
PT 1ch
load current 3ch
IEDsWiring power from outsideI have to.
RTUin a wayModification required
for maintenance
load current
for measurement everyone
coil current for measurementeveryone

## Slide 13: Review the results
Review of development requests
  For power and input/output specifications,confirmed
  DIcontact circuitModification required
  Separation required for coil current input terminal
  RTCno.
Thomas Inquiries
  PoE in the power circuitaboutProceed with inquiry
  external memoryIsare you not using Need to be confirmed