## DU <-> Collective Server
Alarm Setting API
PD | Attribute (Attributes in LUConfig.json) | 61850 DOName (Existence in the Shared Memory) | DataSet | Type | Explanation | Need Extra Implementation?
| msgTime | x | x | Long | Message sent time Timestamp(ms, UTC+0) | x
| contents | x | x | Json Object Array | Array of Json Objects with the following Attribute(eeName ~ HR24_WTHN_SAME_EVNT_B) as attributes | x
| eeName | eeName | Status | String | eeName(A string that can identify the sensor.) ex) K_S730_GLU101_CH03_SWPD_3527485 | x
| PD_TYPE (type) | DevType | x | Status | PD Measurement Target 0: GIS Partial Discharge (GLU), 1 : MTR Body Partial Discharge (MLU), | x
| EVENT_A_ENABLE (event_a, Enable) | x | x | Integer | Whether to use alarm occurrence condition A (0: not used, 1: used) | O
| EVENT_B_ENABLE (event_b, Enable) | x | x | Integer | Whether to use alarm occurrence condition B (0: not used, 1: used) | O
| HR1_WTHN_SAME_EVNT_A (pdhour_lv1_cnt, Setting) | x | x | Integer | Alarm occurrence A-1 condition (number of occurrences of the same type of event within 1 hour) - Same type just means passing the threshold | O
| HR24_WTHN_SAME_EVNT_A (pdday_lv1_cnt, Setting) | x | x | Integer | Alarm occurrence A-2 condition (number of occurrences of the same type of event within 24 hours) | O
| HR24_WTHN_SAME_EVNT_B (pdday_lv2_cnt, Setting) | x | x | Integer | Alarm occurrence condition B (number of occurrences of the same type of event within 24 hours) | O
CB | Attribute (Attributes in LUConfig.json) | 61850 DOName (Existence in the Shared Memory) | DataSet | Type | Explanation | Need Extra Implementation?
| msgTime | x | x | Long | Message sent time Timestamp(ms, UTC+0) | x
| contents | x | x | Json Object Array | Json Object Array with the following Attributes below (eeName ~ GAPTIME_OPEN_CAUT) as an attribute | x
| eeName | eeName | Status | String | eeName(A string that can identify the sensor.) ex) K_S730_GLU101_CH03_CBOP_3527485 | x
| CLOSE_HH_CRTR_VAL (close_hh_crtr_val, Setting) | OpTmCls | Measure | Float | Input time alarm threshold: {value}ms | x
| CON_PART_HH_CRTR_VAL (con_part_hh_crtr_val, Setting) | OpTmOpn | Measure | Float | Opening time alarm threshold: {value}ms | x
| CLOSE_HH_CAUT_ENABLE (close_lv1, Enable) | OpTmWrn | Setting | Integer | Use of alarm for time-lapse alerts (0: not used, 1: used) | x
| CLOSE_HH_CAUT (close_lv1_per, Default) | x | x | Float | {value}% exceeds the threshold for the time-in-use warning alarm | O
| CON_PART_HH_CAUT_ENABLE (trip_lv1, Enable) | x | x | Integer | Use of alarm for opening time caution (0: not used, 1: used) | O
| CON_PART_HH_CAUT (trip_lv1_per, Default) | x | x | Float | Opening time warning alarm threshold exceeded {value}% | O
| COILCURRFLOW_CLOSE_CRTR_VAL (coilcurrflow_close_crtr_val, Setting) | X | X | Float | Coil energization time (activation) alarm threshold: {value}ms | O
| COILCURRFLOW_OPEN_CRTR_VAL (coilcurrflow_open_crtr_val, Setting) | X | X | Float | Coil energization time (release) alarm threshold: {value}ms | O
| COILCURRFLOW_CLOSE_CAUT_CRTR_ENABLE (coilcurrflow_close_caut_crtr, Enable) | X | X | Integer | Whether to use the caution alarm for coil energization time (release) (0: Not used, 1: Used) | O
| COILCURRFLOW_OPEN_CAUT_CRTR (coilcurrflow_open_caut_crtr_val, Setting) | X | X | Float | Coil energization time (release) caution alarm threshold Exceeding {value}% compared to the reference value | O
| GAPTIME_CLOSE_CAUT_ENABLE (gaptime_close_caut, Enable) | X | X | Integer | Whether to use the caution alarm for gap difference (activation) (0: Not used, 1: Used) | O
| GAPTIME_CLOSE_CAUT (gaptime_close_caut_val, Setting) | X | X | Float | Gap difference (activation) caution alarm threshold: {value}ms | O
| GAPTIME_OPEN_CAUT_ENABLE (gaptime_open_caut, Enable) | x | x | Integer | Whether to use the caution alarm for gap difference (release) (0: Not used, 1: Used) | O
| GAPTIME_OPEN_CAUT (gaptime_open_caut_val, Setting) | X | X | Float | Gap difference (release) caution alarm threshold: {value}ms | O
DGA (SIML) | Attribute (Attributes in LUConfig.json) | 61850 DOName (Existence in the Shared Memory) | DataSet | Type | Explanation | Need Extra Implementation?
| msgTime | x | x | Long | Message sent time Timestamp(ms, UTC+0) | x
| contents | x | x | Json Object Array | Json Object Array with the following Attributes below (eeName ~ GAPTIME_OPEN_CAUT) as an attribute | x
| prsrzTime | X | X | String | Transformer pressurization date Ex) 20200724 | O
| eeName | eeName | Status | String | eeName(A string that can identify the sensor.) ex) K_S730_GLU101_CH03_CBOP_3527485 | x
| prsrzType | X | X | Integer | Transformer Early/Mid-Long-Term Classification (0: Early Transformer, 1: Mid-Long-Term Transformer) | O
| dgaSettings | X | X | Json Object Array | Array of Json Objects with attributes (enable, gasName, alarmType, value) below | X
| enable | H2Alm, N2Alm, O2Alm, C2H2Alm, CH4Alm, C2H6Alm C2H4Alm, COAlm, CO2Alm, | Status | Integer | Whether to use the alarm (0: not used, 1: used) | O (Need to check which gas is enabled)
| gasName | X | X | String | Gas name (H2, C2H4, etc.) | X
| alarmType | X | X | String | Alarm type (observation, caution, etc.) | O
| value | H2AlmSpt, N2AlmSpt, O2AlmSpt, C2H2AlmSpt, CH4AlmSpt, C2H6AlmSpt, C2H4AlmSpt, COAlmSpt, CO2AlmSpt | Setting | Integer | Changed settings | X
Bushing (SBSH) | Attribute (Attributes in LUConfig.json) | 61850 DOName (Existence in the Shared Memory) | DataSet | Type | Explanation | Need Extra Implementation?
| msgTime | x | x | Long | Message sent time Timestamp(ms, UTC+0) | x
| contents | x | x | Json Object Array | Json Object Array with the following Attributes below (eeName ~ GAPTIME_OPEN_CAUT) as an attribute | x
| eeName | eeName | Status | String | eeName(A string that can identify the sensor.) ex) K_S730_GLU101_CH03_CBOP_3527485 | x
| BUSHING_TYP | X | X | Integer | Bushing Manufacturing Type - 0: No setting value - 1: Condenser type (OIP) - 2: GIB type - 3: RIP type | O
| CRTR_CAPE_VAL (crtr_cape_val, Setting) | X | X | Float | Initial measured capacitance value: {value}pF | O
| CRTR_CURR_VAL (crtr_cape_val, Setting) | X | X | Float | Initial measured leakage current value: {value}mA | O
| LEAK_CRN_INCR_OBSERVE_ENABLE (lc_lv1, Enable) | BshAlm | Status | Integer | Whether to use leakage current increase observation alarm (0: not used, 1: used) | O (1 : Normal, 2 : Observation, 3 : Caution, 4 : Serious)
| LEAK_CRN_INCR_OBSERVE (lc_lv1_per, Default) | X | X | Float | Leakage current increase observation alarm threshold: {value}% Exceeded | O
| LEAK_CRN_INCR_CAUT_ENABLE (lc_lv2, Enable) | BshAlm | Status | Integer | Whether to use leakage current increase caution alarm (0: not used, 1: used) | O (1 : Normal, 2 : Observation, 3 : Caution, 4 : Serious)
| LEAK_CRN_INCR_CAUT (lc_lv2_per, Default) | X | X | Float | Leakage current increase caution alarm threshold {value}% Exceeded | O
| LEAK_CRN_INCR_CRIL_ENABLE (lc_lv3, Enable) | BshAlm | Status | Integer | Whether to use leakage current increase serious alarm (0: not used, 1: used) | O (1 : Normal, 2 : Observation, 3 : Caution, 4 : Serious)
| LEAK_CRN_INCR_CRIL (lc_lv3_per, Setting) | X | X | Float | Leakage current increase serious alarm threshold {value}% Exceeded | O
| LEAK_CRN_DECR_CAUT_ENABLE (lc_decr_caut, Enable) | X | X | Integer | Leakage current decrease caution alarm (0: not used, 1: used) | O
OLTC (SLTC) | Attribute (Attributes in LUConfig.json) | 61850 DOName (Existence in the Shared Memory) | DataSet | Type | Explanation | Need Extra Implementation?
| msgTime | x | x | Long | Message sent time Timestamp(ms, UTC+0) | x
| contents | x | x | Json Object Array | Json Object Array with the following Attributes below (eeName ~ GAPTIME_OPEN_CAUT) as an attribute | x
| eeName | eeName | Status | String | eeName(A string that can identify the sensor.) ex) K_S730_GLU101_CH03_CBOP_3527485 | x
| MANUFACTURER | x | x | Integer | OLTC Manufacturer - Uses KEPCO ERP substation equipment manufacturer code (0 :Not set, 27 : BULGARIA, 119 : MR) | O
| MIDTAB | x | x | Integer | OLTC Middle tap position | O
| TOTAL_MOTN_HH_CRTR_VAL_GNRLTAB | OpDurWrnLev (No Such data to differentiate middle tab) | Setting | Float | Reference Time of OLTC Total operating time alarm threshold (normal tap): {value}ms | x
| TOTAL_MOTN_HH_CRTR_VAL_MIDTAB | OpDurWrnLev (No Such data to differentiate middle tab) | Setting | Float | Reference Time of OLTC Total Operating Time Alarm Threshold (Middle Tab): {Value}ms | x
| TOTAL_MOTN_HH_CAUT_GNRL TAB_ENABLE | x | x | Integer | OLTC Total Operation Time Caution (General Tab) Alarm Usage (0: Not used, 1: Used) | O
| TOTAL_MOTN_HH_CAUT_GNRL TAB | x | x | Float | OLTC Total Operating Time Caution (General Tab) Alarm Reference Value ±{Value}% | O
| TOTAL_MOTN_HH_CAUT_MIDTAB_ENABLE | x | x | Integer | OLTC Total Operation Time Caution (Middle Tab) Alarm Usage (0: Not used, 1: Used) | O
| TOTAL_MOTN_HH_CAUT_MIDTAB | x | x | Float | OLTC Total Operating Time Caution (Middle Tab) Alarm Reference Value ±{Value}% | O
| START_ISEG_MAX_CRN_CRTR_VAL | MDAAlmLev (No Such data to differentiate middle tab) | Status | Float | Inrush section maximum current alarm threshold: {value} mA | X
| START_ISEG_MOTN_HH_CRTR_VAL_GNRLTAB | OpDurAlmLev (No Such data to differentiate middle tab) | Setting | Float | Inrush section operation time alarm threshold (general tab): {value} ms | X
| START_ISEG_MOTN_HH_CRTR_VAL_MIDTAB | OpDurAlmLev (No Such data to differentiate middle tab) | Setting | Float | Inrush section operation time alarm threshold (middle tab): {value} ms | X
| START_ISEG_MAX_CRN_CAUT_ENABLE | x | x | Integer | Whether to use the alarm for maximum current warning in the inrush section (0: not used, 1: used) | O
| START_ISEG_MAX_CRN_CAUT | x | x | Float | Maximum current in the inrush section Caution alarm threshold value ±{value}% | O
| START_ISEG_MOTN_HH_CAUT_GNRLTAB_ENABLE | x | x | Integer | Inrush section operation time (general tab) Caution alarm Use or not (0: not used, 1: used) | O
| START_ISEG_MOTN_HH_CAUT_MIDTAB | x | x | Float | Inrush section operation time (middle tap) Caution alarm Reference value ±{value}% | O
| NORM_ISEG_MAX_HH_CRTR_VAL | x | x | Float | Normal section maximum current alarm threshold {value} mA | O
| NORM_ISEG_MOTN_HH_CRTR_VAL_GNRLTAB | x | x | Float | Normal section operation time (general tab) alarm threshold: {value} ms | O
| NORM_ISEG_MOTN_HH_CRTR_VAL_MIDTAB | x | x | Float | Normal section operation time (middle tap) alarm threshold: {value} ms | O
| NORM_ISEG_MAX_CRN_CAUT_ENABLE | x | x | Integer | Use of alarm for maximum current warning in normal section (0: not used, 1: used) | O
| NORM_ISEG_MAX_CRN_CAUT | x | x | Float | Normal section maximum current warning alarm threshold value ±{value}% | O
| NORM_ISEG_MOTN_HH_CAUT_GNRLTAB_ENABLE | x | x | Integer | Use of alarm for maximum Operation time warning (general tab) in normal section (0: not used, 1: used) | O
| NORM_ISEG_MOTN_HH_CAUT_GNRLTAB | x | x | Float | Normal section operation time (general tab) Caution alarm Reference value ±{value}% | O
| NORM_ISEG_MOTN_HH_CAUT_MIDTAB_ENABLE | x | x | Integer | Use of alarm for maximum Operation time warning (middle tab) in normal section (0: not used, 1: used) | O
| NORM_ISEG_MOTN_HH_CAUT_MIDTAB | x | x | Float | Normal section operation time (middle tab) Caution alarm Reference value ±{value}% | O
Event Setting API
PD | Attribute (Attributes in LUConfig.json) | 61850 DOName (Existence in the Shared Memory) | DataSet | Type | Explanation | Need Extra Implementation?
| msgTime | x | x | Long | Message sent time Timestamp(ms, UTC+0) | x
| contents | x | x | Json Object Array | Array of Json Objects with the following Attribute(eeName ~ HR24_WTHN_SAME_EVNT_B) as attributes | x
| eeName | eeName | Status | String | eeName(A string that can identify the sensor.) ex) K_S730_GLU101_CH03_SWPD_3527485 | x
| THRS_VAL (maxdbm_lv1_val, Setting) | EvtAmpThre1 | Setting | Integer | Threshold of event occurrence condition A [dBm] | x
| THRS_PPS_VAL (maxdbm_lv2_val, Setting) | EvtAmpThre2 | Setting | Integer | Threshold of event occurrence condition B [dBm] | x
| PPS_VAL | EvtPpsThre2 | Setting | Integer | Measured PPS level that triggered the event occurrence condition B | x
| EVNT_OCCR_CNT | RsOpCnt | Setting | Integer | Minimum count of PD occurrences for occuring PD event | x
CB | Attribute (Attributes in LUConfig.json) | 61850 DOName (Existence in the Shared Memory) | DataSet | Type | Explanation | Need Extra Implementation?
| msgTime | x | x | Long | Message sent time Timestamp(ms, UTC+0) | x
| contents | x | x | Json Object Array | Array of Json Objects with the following Attribute(eeName ~ HR24_WTHN_SAME_EVNT_B) as attributes | x
| eeName | eeName | Status | String | eeName(A string that can identify the sensor.) ex) K_S730_GLU101_CH03_SWPD_3527485 | x
| CRTR_TYP | x | x | Integer | Reference Waveform Type (0: Trip, 1: Close) | O
| CRTR_WV_TIME | x | x | String | YYYYMMDDHHMMSSsss (20200723203400289 : 2020년 07월 23일 20시 34분 00초 289ms) | O
Alarm Setting Change API
| Attribute (Attributes in LUConfig.json) | 61850 DOName (Existence in the Shared Memory) | DataSet | Type | Explanation | Need Extra Implementation?
| msgTime | x | x | Long | Message sent time Timestamp(ms, UTC+0) | x
| contents | x | x | Json Object Array | Array of Json Objects with the following Attribute(eeName ~ HR24_WTHN_SAME_EVNT_B) as attributes | x
| eeName | eeName | Status | String | eeName(A string that can identify the sensor.) ex) K_S730_GLU101_CH03_SWPD_3527485 | x
| revisedTime | x | x | Long | Alarm setting change time Timestamp (ms, UTC+0) | O
| dchgs | x | x | Json Object Array | Array of Json Objects with the following Attribute(key, value) as Attribute | O
| key | x | x | String | Alarm Setting Attribute Name | O
| value | x | x | Integer or Float | Changed alarm settings | O
| comment | x | x | String | Reason for changing alarm settings | O
| username | x | x | String | Name or ID of the person who changed the alarm setting | O
DGA Alarm Setting Change API
| Attribute (Attributes in LUConfig.json) | 61850 DOName (Existence in the Shared Memory) | DataSet | Type | Explanation | Need Extra Implementation?
| msgTime | x | x | Long | Message sent time Timestamp(ms, UTC+0) | x
| contents | x | x | Json Object Array | Array of Json Objects with the following Attribute(eeName ~ HR24_WTHN_SAME_EVNT_B) as attributes | x
| eeName | eeName | Status | String | eeName(A string that can identify the sensor.) ex) K_S730_GLU101_CH03_SWPD_3527485 | x
| prsrzType | x | x | Integer | Transformer Early/Mid-Long-Term Classification(0: Early Transformer, 1: Mid-Long-Term Transformer) | O
| revisedTime | x | x | Long | Alarm setting change time Timestamp (ms, UTC+0) | O
| dgaSettings | x | x | Json Object Array | Array of Json Objects with the following Attributes (enable, gasName, alarmType, value) | O
| enable | x | x | Integer | Whether to use the alarm (0: not used, 1: used) | O
| gasName | x | x | String | Gas names (H2, C2H4, etc.) | O
| alarmType | x | x | String | Alarm type (observation, caution, etc.) | O
| value | x | x | String | Changed alarm settings | O
| comment | x | x | String | Reason for changing alarm settings | O
| username | x | x | String | Name or ID of the person who changed the alarm setting | O
Event Setting Change API
| Attribute (Attributes in LUConfig.json) | 61850 DOName (Existence in the Shared Memory) | DataSet | Type | Explanation | Need Extra Implementation?
| msgTime | x | x | Long | Message sent time Timestamp(ms, UTC+0) | x
| contents | x | x | Json Object Array | Array of Json Objects with the following Attribute(eeName, revisedTime) as attributes | x
| eeName | eeName | Status | String | eeName(A string that can identify the sensor.) ex) K_S730_GLU101_CH03_SWPD_3527485 | x
| revisedTime | x | x | Long | Change alarm settings time Timestamp(ms, UTC+0) | x
| dchgs | x | x | Json Object Array | Array of Json Objects with the following Attributes (key, value) as Attributes key | x
| key | x | x | String | Event Setting Attribute Name | x
| value | x | x | Integer | Changed alarm settings value | x
| comment | x | x | String | Reason for changing alarm settings | x
| username | x | x | String | Name or ID of the person who changed the alarm setting | x

## PD DataSet
| 로컬유닛→진단유닛 | 진단유닛→HMI서버
Status | OpCnt (작동 횟수) | OpCnt (작동 횟수)
| MoDevComF (통신상태이상) | MoDevComF (통신상태이상)
| MoDevFlt (하드웨어폴트) | MoDevFlt (하드웨어폴트)
| TrendTransF (Trend file ready flag) | TrendTransF (Trend file ready flag)
| RTTransF (Realtime file read flag) | RTTransF (Realtime file read flag)
Measurands | PriHarRte (60Hz 상관성) | PriHarRte (60Hz 상관성)
| SecHarRte (120Hz 상관성) | SecHarRte (120Hz 상관성)
| DschCnt (신호발생 횟수) | DschCnt (신호발생 횟수)
| DschCntPhRs (위상별 최대 신호발생 횟수 | DschCntPhRs (위상별 최대 신호발생 횟수)
| AppPaDsch (최대신호크기) | AppPaDsch (최대신호크기)
| MaxPaDschPh (최대 신호 크기 위상) | MaxPaDschPh (최대 신호 크기 위상)
| UhfPaDsch (UHF신호크기) | UhfPaDsch (UHF신호크기)
Setting Values | EvtAmpThre1 (Event Amplitude Level Threshold) | EvtAmpThre1 (Event Amplitude Level Threshold)
| EvtAmpThre2 (Event Amplitude Level Threshold) | EvtAmpThre2 (Event Amplitude Level Threshold)
| EvtPpsThre1 (Event pps Threshold) | EvtPpsThre1 (Event pps Threshold)
| EvtPpsThre2 (Event pps Threshold) | EvtPpsThre2 (Event pps Threshold)
| PlsLvlThre (Pulse Level Threshold) | PlsLvlThre (Pulse Level Threshold)
| AttSet (Attenuation Setting) | AttSet (Attenuation Setting)
| PhShift (Phase shift) | PhShift (Phase shift)
| CtrHz (측정장치의 중심 주파수) | CtrHz (측정장치의 중심 주파수)
| BndWid (측정장치의 Bandwidth) | BndWid (측정장치의 Bandwidth)
| RsOpCnt(이벤트 연속발생 시간(초)) | RsOpCnt(이벤트 연속발생 시간(초))
진단값 | EvtLvlSt (Event Level State) | PaDschAlm (부분방전경보)
| EvtTransF (Event file read flag) | EvtLvlSt (Event Level State)
Prob0~11 (진단값)
EvtTransF (Event file read flag)
(제외 항목) | DevType (측정 대상) | DevType (측정 대상)
| DevV (대상 전압) | DevV (대상 전압)
| SensorType (센서 타입) | SensorType (센서 타입)
| MeasureUnit (측정값단위) | MeasureUnit (측정값단위)
PaDschAlm (부분 방전 경보)
Prob0~11 (진단값)

## Bushing DataModel
데이터 모델
| 이름 | CDC | 설명 | LU | MU
| Mod | INC |  | ○ | ○
| Beh | INS |  | ○ | ○
| Health | INS |  | ○ | ○
| NamPlt | LPL |  | ○ | ○
| EEName | DPL |  | × | ○
Status
| BshAlm | INS | 부싱알람 | × | ○
| EvtTransF | INS | 이벤트 발생 플래그 | ○ | ○
| RTTransF | INS | 실시간 파일 발생 플래그 | ○ | ○
| MoDevComF | SPS | 통신상태 | ○ | ○
| MoDevFlt | SPS | 하드웨어폴트 | ○ | ○
Measurands
| React | MV | Capacitance 비율 | ○ | ○ | 비율은 뭐지? 아래의 capacitance 설정값에 대한 capacitance 계측값의 비율인가?
| AbsReact | MV | Capacitance 값 | ○ | ○
| LosFact | MV | 손실계수 | ○ | ○ | Dissipation factor (tan delta)?
| Vol | MV | 전압 값 | ○ | ○
| DisplA | MV | 변위전류 | ○ | ○ | 변위전류? Capacitor와 같이 떨어져 이는 두 전극 사이에 흐르는 전류? 어떻게 계측?
| LeakA | MV | 누설전류 값 | ○ | ○
| LeakAphs | MV | 누설전류위상 | ○ | ○
| Volphs | MV | 전압위상 | ○ | ○
| PF | MV | 역률 | ○ | ○
| UnblA | MV | 불평형전류 | ○ | ○
| UnblAphs | MV | 불평형전류 위상 | ○ | ○
Settings
| RefReact | ASG | Capacitance 설정값 | × | ○
| RefPF | ASG | 역률 설정값 | × | ○
| RefV | ASG | 전압 설정값 | × | ○

## Bushing DataSet
DataSet
|  | 로컬유닛→진단유닛 | 구현 여부 | 진단유닛→HMI서버
| Status | EvtTransF (이벤트 발생 Flag) |  | EvtTransF (이벤트 발생 Flag)
|  | RsOpCnt (동작횟수) |  | BSHAlm (알람 발생)
|  | MoDevComF (통신상태) |  | RsOpCnt (동작횟수)
|  | MoDevFlt (H/W Fault) |  | MoDevComF (통신상태)
MoDevFlt (H/W Fault)
| Measurands | React(Capacitance 비율) |  | React(Capacitance 비율)
|  | AbsReact(Capacitance 값) | OK | AbsReact(Capacitance 값)
|  | LosFact(손실계수) | OK | LosFact(손실계수)
|  | Vol(전압) | OK | Vol(전압)
|  | DisplA(변위전류) | OK | DisplA(변위전류)
|  | LeakA(누설전류) | OK | LeakA(누설전류)
|  | LeakAphs(누설전류위상) | OK | LeakAphs(누설전류위상)
|  | Volphs(전압위상) | OK | Volphs(전압위상)
|  | PF(역률) | OK | PF(역률)
|  | UnblA(불평형 전류) | OK | UnblA(불평형 전류)
|  | UnblAphs(불평형전류 위상) | OK | UnblAphs(불평형전류 위상)

## 차단기 DataModel
데이터 모델
| 이름 | CDC | 설명 | LU | MU
| Mod | INC |  | ○ | ○
| Beh | INS |  | ○ | ○
| Health | INS |  | ○ | ○
| NamPlt | LPL |  | ○ | ○
| EEName | DPL |  | × | ○
Status
| ColOpn | SPS | 트립코일 개방명령 | ○ | ○ | 투입코일 투입명령은 없나?
| AbrAlm | SPS | 접점마모 알람 | × | ○ | 접점 마모 판단 기준은 뭐지?
| AbrWrn | SPS | 접점마모 경보 | × | ○
| OpTmAlm | SPS | 스위치동작시간초과 | ○ | ○
| ColAlm | SPS | 코일알람 | × | ○ | 코일 알람이 뭐지? 코일의 전류가 기준치를 초과한 것인가?
| OpCntAlm | SPS | 알람레벨초과동작횟수 | × | ○
| OpCntWrn | SPS | 경고레벨초과동작횟수 | × | ○
| OpTmWrn | SPS | 경고레벨동작시간 | × | ○
| OpTmh | INS | 설치시간설정시간 | × | ○ | 설치시간 설정시간이 뭐지?
| EvtTransF | INS | 이벤트 발생 플래그 | ○ | ○
| RsOpCnt | ING | 차단기 동작횟수 | ○ | ○
| MoDevComF | SPS | 통신상태 | ○ | ○ | ACQ와의 통신 상태?
| MoDevFlt | SPS | 하드웨어폴트 | ○ | ○ | ACQ의 H/W fault 상태?
| CbAlm | INS | CB Alarm | × | ○
Measurands
| AccAbr | MV | 누적마모량 | ○ | ○ | 마모량을 어떻게 알지?
| SwA | MV | 최근차단전류량 | ○ | ○
| ActAbr | MV | 최근마모량 | ○ | ○ | 마모량을 어떻게 알지?
| AuxSwTmOpn | MV | 개방 보조 스위치 타이밍 | ○ | ○
| AuxSwTmCls | MV | 투입 보조 스위치 타이밍 | ○ | ○
| RctTmOpn | MV | 개방 반응시간 | ○ | ○
| RctTmCls | MV | 투입 반응시간 | ○ | ○
| OpSpdOpn | MV | 개방 동작 속도 | ○ | ○ | 속도는 어떤 의미인가? 이동거리라는 것이 있는가?
| OpSpdCls | MV | 투입 동작 속도 | ○ | ○ | 속도는 어떤 의미인가? 이동거리라는 것이 있는가?
| OpTmOpn | MV | 개방 동작 시간 | ○ | ○
| OpTmCls | MV | 투입 동작 시간 | ○ | ○
| Stk | MV | 접점접촉 | ○ | ○ | "접점접촉"이라는 계측값이 뭐지?
| OvStkOpn | MV | 개방과접촉 | ○ | ○ | "개방과접촉"이라는 계측값이 뭐지?
| OvStkCls | MV | 폐쇄과접촉 | ○ | ○ | "폐쇄과접촉"이라는 계측값이 뭐지?
| ColA | MV | 코일전류 | ○ | ○
| Tmp | MV | 온도 | ○ | ○ | 온도?
| ColV | MV | 코일전압 | ○ | ○ | "코일전압"은 어떤 계측값인가? 코일전류의 적분값?
| ClsColA | MV | 최근투입코일전류량 | ○ | ○
| OpnColA | MV | 최근차단코일전류량 | ○ | ○
| BctA | MV | 모선전류A상 | ○ | ○
| BctB | MV | 모선전류B상 | ○ | ○
| BctC | MV | 모선전류C상 | ○ | ○
Settings
| AbrAlmLev | ASG | 마모 알람 설정치 | × | ○
| AbrWrnLev | ASG | 마모 경고 설정치 | × | ○
| OpAlmTmh | ING | 동작시간 알람 설정치 | × | ○
| OpWrnTmh | ING | 동작시간 경고 설정치 | × | ○
| OpAlmNum | ING | 동작횟수 알람 설정치 | × | ○
| OpWrnNum | ING | 동작횟수 경고 설정치 | × | ○

## 차단기DataSet
DataSet
|  | 로컬유닛→진단유닛 | 진단유닛→HMI서버
| Status | EvtTransF (이벤트 발생 Flag) | EvtTransF (이벤트 발생 Flag)
|  | RsOpCnt (동작횟수) | CbAlm (알람 발생)
|  | MoDevComF (통신상태) | RsOpCnt (동작횟수)
|  | MoDevFlt (H/W Fault) | MoDevComF (통신상태)
MoDevFlt (H/W Fault)

## 차단기 FileFormat
File Format
| 구 분 | Size |  | type | 내 용 | 비 고 |  |  |  |  | LU | MU
(Byte)
| ② CBCM | 98 | 1 | uint8 | 이벤트 타입 | Trip=0x55, Close=0xAA |  |  |  |  | O | O
|  | (정보) | 4 | uint32 | 이벤트 시간 | 년, 월, 일, 시, 분, 초 (UTC+9) |  |  |  |  | O | O
| 98+29952 |  | 4 | uint32 | 이벤트 시간 | msec (예: 값 200은 200ms로 인식) |  |  |  |  | O | O
| 30050 |  | 1 | uint8 | 경보레벨(uint8) | 알람이 발생하면 원인(진단Unit이 진단 결과로 알람 Enum값으로 채움) |  |  |  |  | X | O
|  |  | 4 | float | contact duty A | 차단전류 A 주) 1 |  |  |  |  | X | O
|  |  | 4 | float | contact duty B | 차단전류 B 주) 2 |  |  |  |  | X | O
|  |  | 4 | float | contact duty C | 차단전류 C 주) 3 |  |  |  |  | X | O
|  |  | 4 | float | accum c.duty A | 누적차단전류 A 주) 1 |  |  |  |  | X | O
|  |  | 4 | float | accum c.duty B | 누적차단전류 B 주) 2 |  |  |  |  | X | O
|  |  | 4 | float | accum c.duty C | 누적차단전류 C 주) 3 |  |  |  |  | X | O
|  |  | 4 | float | T1 코일 적분 값 | ∫ABS(i)dt (AS) (= TripProfileArea : sec) |  |  |  |  | X | O | 전류절대값를 적분해서 전압을 얻겠다는 것인가?
|  |  | 4 | float | T1 코일 최대 전류 | Peak 전류 (= TripCoilPeak) |  |  |  |  | X | O
|  |  | 4 | float | T1 코일 여자 시간 | 여자코일 시작(상승)~끝(하강) 지점까지 시간 |  |  |  |  | X | O
[6 empty] | (= TripCurrflow : msec) |  |  |  |  | X | O
|  |  | 4 | float | T2 코일 적분 값 | ∫ABS(i)dt (AS) (= TripProfileArea : sec) |  |  |  |  | X | O | 전류절대값를 적분해서 전압을 얻겠다는 것인가?
|  |  | 4 | float | T2 코일 최대 전류 | Peak 전류 (= TripCoilPeak) |  |  |  |  | X | O
|  |  | 4 | float | T2 코일 여자 시간 | 여자코일 시작(상승)~끝(하강) 지점까지 시간 |  |  |  |  | X | O
[6 empty] | (= TripCurrflow : msec) |  |  |  |  | X | O
|  |  | 4 | float | C 코일 적분 값 | ∫ABS(i)dt (AS) (= CloseProfileArea : sec) |  |  |  |  | X | O | 전류절대값를 적분해서 전압을 얻겠다는 것인가?
|  |  | 4 | float | C 코일 최대 전류 | Peak 전류 (= CloseCoilPeak) |  |  |  |  | X | O
|  |  | 4 | float | C 코일 여자 시간 | 여자코일 시작(상승)~끝(하강) 지점까지 시간 |  |  |  |  | X | O
[6 empty] | (= CloseCurrflow : msec) |  |  |  |  | X | O
|  |  | 4 | float | A 접점 동작시간 | 여자시간 ~ A접점변화 까지 시간 |  |  |  |  | X | O
|  |  | 4 | float | B 접점 동작시간 | 여자시간 ~ B접점변화 까지 시간 |  |  |  |  | X | O
|  |  | 4 | float | 상별 차단/ | 단위 : msec 주) 1 |  |  |  |  | X | O
[5 empty] | 투입 시간(A상) | [5 empty] | X | O
|  |  | 4 | float | 상별 차단/ | 단위 : msec 주) 2 |  |  |  |  | X | O
[5 empty] | 투입 시간(B상) | [5 empty] | X | O
|  |  | 4 | float | 상별 차단/ | 단위 : msec 주) 3 |  |  |  |  | X | O
[5 empty] | 투입 시간(C상) | [5 empty] | X | O
|  |  | 4 | uint32 | OpCnt | 차단기 동작카운트 (Trip 동작 시) |  |  |  |  | X | O
|  |  | 2 | uint16 | smpPerCyc | 샘플링 수 (128 고정 값) |  |  |  |  | X | O
|  | 98 | 2 | uint16 | cycCnt | cycle 수 ( 18 고정 값) |  |  |  |  | X | O
|  | 29952 | 4608 | uint16 | Trip1_CoilCurrent | 파형데이터 (T1-Coil) |  |  |  |  | O | O | = sizeof(uint16) * 128samples/cycle * 18cycles
|  | (파형) | 4608 | uint16 | Trip2_CoilCurrent | 파형데이터 (T2-Coil) |  |  |  |  | O | O | = sizeof(uint16) * 128samples/cycle * 18cycles
|  |  | 4608 | uint16 | CloseCoilCurrent | 파형데이터 (C-Coil) |  |  |  |  | O | O | = sizeof(uint16) * 128samples/cycle * 18cycles
|  |  | 4608 | uint16 | PhaseCurrentA | 파형데이터 (A상) 주) 1 |  |  |  |  | O | O
[6 empty] | (2byte * 18cycle * 128sample = 4608) |  |  |  |  | O | O
|  |  | 4608 | uint16 | PhaseCurrentB | 파형데이터 (B상) 주) 2 |  |  |  |  | O | O
[6 empty] | (2byte * 18cycle * 128sample = 4608) |  |  |  |  | O | O
|  |  | 4608 | uint16 | PhaseCurrentC | 파형데이터 (C상) 주) 3 |  |  |  |  | O | O
[6 empty] | (2byte * 18cycle * 128sample = 4608) |  |  |  |  | O | O
|  |  | 2304 | char | InitiateAndContact | 파형데이터 (A/B 접점, ON=1, OFF=0) |  |  |  |  | O | O | = sizeof(char) * 128samples/cycle * 18cycles
[6 empty] | (1byte * 18cycle * 128sample = 2304) |  |  |  |  | O | O
[6 empty] | 7bit(MSB) | 6bit | ... | 1bit | 0bit | O | O
| 30050 | 29952 |  |  |  | - | - | ... | b접점 | a접점 | O | O
| 주) 1 : | - 3상 일괄형 : A상으로 처리
- 3상 분리형 : 각 상에 대한 정보 값 설정 (A, B 또는 C상 값 정보)
| 주) 2 : | - 3상 일괄형 : B상으로 처리 - 3상 분리형 : NULL
| 주) 3 : | - 3상 일괄형 : C상으로 처리 - 3상 분리형 : NULL

## 유중가스DataModel
데이터 모델
| 이름 | CDC | 설명 | LU | MU | 비고
| Mod | INC |  | ○ | ○
| Beh | INS |  | ○ | ○
| Health | INS |  | ○ | ○ | 센서상태
| NamPlt | LPL |  | ○ | ○
| EEName | DPL |  | × | ○
Status
| InsAlm | SPS | 절연유 알람 | × | ○
| H2Alm | SPS | H2 Alarm | × | ○ | 수소
| N2Alm | SPS | N2 Alarm | × | ○ | 질소
| O2Alm | SPS | O2 Alarm | × | ○ | 산소
| C2H2Alm | SPS | C2H2 Alarm | × | ○ | 아세틸렌
| CH4Alm | SPS | CH4 Alarm | × | ○ | 메탄
| C2H6Alm | SPS | C2H6 Alarm | × | ○ | 에탄
| C2H4Alm | SPS | C2H4 Alarm | × | ○ | 에틸렌
| COAlm | SPS | CO Alarm | × | ○ | 일산화탄소
| CO2Alm | SPS | CO2 Alarm | × | ○ | 이산화탄소
| MstAlm | SPS | Moisture Alarm | × | ○ | 수분 (H2O)
| C3H8Alm | SPS | C3H8 Alarm | × | ○ | 프로판
| MoDevComF | SPS | 통신상태 | ○ | ○
| MoDevFlt | SPS | 하드웨어폴트 | ○ | ○
| DgaAlm | INS | DGA Alarm | × | ○
Measurands
| Tmp | MV | H2 ppm | ○ | ○ | 절연유 온도
| Lev | MV | N2 ppm | ○ | ○ | 절연유 레벨
| Pres | MV | O2 ppm | ○ | ○ | 절연유 압력
| H2Oppm | MV | H2O ppm | ○ | ○ | 물
| H2ppm | MV | H2 ppm | ○ | ○ | 수소
| N2ppm | MV | N2 ppm | ○ | ○ | 질소
| COppm | MV | CO ppm | ○ | ○ | 일산화탄소
| CO2ppm | MV | CO2 ppm | ○ | ○ | 이산화탄소
| CH4ppm | MV | CH4 ppm | ○ | ○ | 메탄
| C2H2ppm | MV | C2H2 ppm | ○ | ○ | 아세틸렌
| C2H4ppm | MV | C2H4 ppm | ○ | ○ | 에틸렌
| C2H6ppm | MV | C2H6 ppm | ○ | ○ | 에탄
| O2ppm | MV | O2 ppm | ○ | ○ | 산소
| C3H8ppm | MV | C3H8 ppm | O | O | 프로판
Settings
| H2AlmSpt | ASG | H2 Alarm set-point | × | ○ | 수소
| N2AlmSpt | ASG | N2 Alarm set-point | × | ○ | 질소
| O2AlmSpt | ASG | O2 Alarm set-point | × | ○ | 산소
| C2H2AlmSpt | ASG | C2H2 Alarm set-point | × | ○ | 아세틸렌
| CH4AlmSpt | ASG | CH4 Alarm set-point | × | ○ | 메탄
| C2H6AlmSpt | ASG | C2H6 Alarm set-point | × | ○ | 에탄
| C2H4AlmSpt | ASG | C2H4 Alarm set-point | × | ○ | 에틸렌
| COAlmSpt | ASG | CO Alarm set-point | × | ○ | 일산화탄소
| CO2AlmSpt | ASG | CO2 Alarm set-point | × | ○ | 이산화탄소
| MstAlmSpt | ASG | Moisture Alarm set-point | × | ○ | 수분
| C3H8AlmSpt | ASG | C3H8 Alarm set-point | X | O | 프로판

## 유중가스 DataSet
DataSet
|  | 로컬유닛→진단유닛 | 진단유닛→HMI서버
| Status | MoDevComF | DgaAlm
|  | MoDevFlt | H2Alm
N2Alm
O2Alm
C2H2Alm
CH4Alm
C2H6Alm
C2H4Alm
COAlm
COAlm
MstAlm
| Measurands | H2ppm | H2ppm
|  | N2ppm | N2ppm
|  | O2ppm | O2ppm
|  | C2H2ppm | C2H2ppm
|  | CH4ppm | CH4ppm
|  | C2H6ppm | C2H6ppm
|  | C2H4ppm | C2H4ppm
|  | COppm | COppm
|  | COppm | COppm
|  | H2Oppm | H2Oppm

## OLTC DataModel
데이터 모델
| 이름 | CDC | 설명 | LU | MU
| Mod | INC |  | ○ | ○
| Beh | INS |  | ○ | ○
| Health | INS |  | ○ | ○
| NamPlt | LPL |  | ○ | ○
| EEName | DPL |  | × | ○
Status
| OilFil | SPS | 오일필터 동작상태 | ○ | ○ | 이제는 미사용?
| MotDrvBlk | SPS | 구동모터 과전류차단 중 | ○ | ○ | 과전류 차단 중이라는 것은 어떻게 알지? 모터에서 오는 접점은 업음
| VacCelAlm | SPS | 감압셀 회로상태 | ○ | ○ | 감압셀 회로?
| OilFilTr | SPS | 오일필터 트립 | ○ | ○ | 이제는 미사용?
| MotDrvAAlm | SPS | 구동모터 전류알람 | × | ○
| MotDrvAWrn | SPS | 구동모터 전류경보 | × | ○
| TorqAlm | SPS | 구동모터 토크알람 | × | ○
| TorqWrn | SPS | 구동모터 토크경보 | × | ○
| OpDurAlm | SPS | LTC 동작 시간 알람 | × | ○
| OpDurWrn | SPS | LTC 동작 시간 경보 | × | ○
| OpCntAlm | SPS | LTC 동작 횟수 알람 | × | ○
| OpCntWrnl | SPS | LTC 동작 횟수 경보 | × | ○
| ArbPrtAlm | SPS | LTC 마모 알람 | × | ○
| ArbPrtWrn | SPS | LTC 마모 경보 | × | ○
| OilTmpDifAlm | SPS | LTC-변압기 오일 온도차이 알람 | × | ○ | 이제는 미사용?
| OilFilCnt | INS | 오일필터 여과 횟수 | ○ | ○ | 이제는 미사용?
| OilFilCntAlm | SPS | 오일필터 오일 여과 횟수 알람 | × | ○ | 이제는 미사용?
| OilFilCntWrn | SPS | 오일필터 오일 여과 횟수 경고 | × | ○ | 이제는 미사용?
| EvtTransF | INS | 이벤트 발생 플래그 | ○ | ○
| RsOpCnt | ING | LTC 동작횟수 | ○ | ○
| MoDevComF | SPS | 통신상태 | ○ | ○
| MoDevFlt | SPS | 하드웨어폴트 | ○ | ○
| LtcAlm | INS | LTC Alarm | × | ○
Measurands
| Torq | MV | 구동모터 토크 | ○ | ○ | 구동모터 토크는 어떻게 계측하지?
| MotDrvA | MV | 구동모터 전류 | ○ | ○
| AbrPrt | MV | LTC 마모 정도 | ○ | ○ | LTC 마모를 어떻게 계측하지?
| OpDur | MV | LTC 동작 시간 | ○ | ○
| OilTmpDif | MV | LTC-변압기 온도차이 | ○ | ○ | 이제는 미사용?
| OutTmp | MV | 외기온도 | ○ | ○
| MotDrvAphsA | MV | 구동모터 A상 전류 | ○ | ○
| MotDrvAphsB | MV | 구동모터 B상 전류 | ○ | ○
| MotDrvAphsC | MV | 구동모터 C상 전류 | ○ | ○
| OilFilTmp | MV | 절연유 온도 | ○ | ○ | 이제는 미사용?
| OilFilBar | MV | 절연유 압력 | ○ | ○ | 이제는 미사용?
| OilFilMst | MV | 절연유 수분 함유량 | ○ | ○ | 이제는 미사용?
Controls
| OpCntRs | INC | LTC 동작횟수 | ○ | ○
Settings
| MDAAlmLev | ASG | 구동 모터 전류 알람 임계값 | × | ○
| MDAWrnLev | ASG | 구동 모터 전류 경고 임계값 | × | ○
| TorqAlmLev | ASG | 구동 모터 토크 알람 임계값 | × | ○
| TorqWrnLev | ASG | 구동 모터 토크 경고 임계값 | × | ○
| OpDurAlmLev | ASG | LTC 동작시간 알람 임계값 | × | ○ | 동작횟수 알람 임계값 설정은 없나?
| OpDurWrnLev | ASG | LTC 동작시간 경고 임계값 | × | ○ | 동작횟수 경고 임계갑 설정은 없나?
OLTC 감시는 OLTC 동작 때 마다 데이터를 수신하는 것을 기준으로 한다.

## OLTC DataSet
DataSet
|  | 로컬유닛→진단유닛 | 구현 여부 | 진단유닛→HMI서버
| Status | EvtTransF (이벤트 발생 Flag) |  | EvtTransF (이벤트 발생 Flag)
LTCAlm (알람 발생)
| Measurands | MotDrvAphsA (모터 A상 전류) | OK | MotDrvAphsA (모터 A상 전류)
|  | MotDrvAphsB (모터 B상 전류) | OK | MotDrvAphsB (모터 B상 전류)
|  | MotDrvAphsC (모터 C상 전류) | OK | MotDrvAphsC (모터 C상 전류)
|  | OpDur (최종 이벤트 동작시간) |  | OpDur (최종 이벤트 동작시간)
|  | OilFilTmp (유온도) | 미사용 | OilFilTmp (유온도)
|  | OilFilBar (유압) | 미사용 | OilFilBar (유압)
|  | OilFilMst (유수분함유량) | 미사용 | OilFilMst (유수분함유량)
|  | OutTmp(외기온도) | OK | OutTmp(외기온도)

## OLTC FileFormat
File Format
| Size |  | 내 용 | 비 고
(Byte)
| 691230 | 4 | 생성시각(uint32) | 구동모터 동작 이벤트 발생 시각(UTC+9) | 정보 수신 시각
|  | 1 | 경보레벨(uint32) | Null | 0
|  | 4 | 동작 시간(int32) | msec | 측정한 시간값
|  | 4 | 동작 횟수(int32) | 구동 모터 동작 횟수 | ?
|  | 4 | 최대 전류(float) |  | ?
|  | 4 | 평균 전류(float) |  | ?
|  | 4 | 위상수(uint32) | 128 sample | 128
|  | 1 | Single data length(char) | 2 | 2
|  | 4 | 데이터 샘플 개수(uint32) | MAX : 15sec * 60cycle * 128sample=115200 | 115200
|  | 230400 | A상 전류(int16) | 2byte * 128sample * 60cycle * 15sec | 115200개의 전류값 수
|  | 230400 | B상 전류(int16) | 2byte * 128sample * 60cycle * 15sec | 115200개의 전류값 수
|  | 230400 | C상 전류(int16) | 2byte * 128sample * 60cycle * 15sec | 115200개의 전류값 수

## OLTC관련 추가사항
기존 SPDC 모델의 DevType수정
이름 | CDC | 설명 | LU | MU | 비고
DevType | INS | 장치타입 | O | O | 1:GIS 2:Mtr 3:Cable 4:OLTC 999:Noise
파일 이름 파형 코드 추가
LN | FileType | Code
SPDC(OLTC) | Realtime | 70
| Trend | 71
| Event | 72
OLTC 부분방전은 계속 유지되나?